## Sheet1
[11 empty] | Research Scope |  |  | Dynamic Modeling for Application | [10 empty] | Dynamic Modeling for Testbed | [13 empty] | Evaluation |  |  |  |  | Application Deployment
Study_ID | Report_ID | Article Title | Authors | Author Full Names | Publication Date | Publication Year | DOI Link | Author Keywords | Application Domain | Journal | Research Gap | Objectives | Target System Scale | Dynamic Model Target | Dynamic Modeling Scale | Model Paradigm | Modeling Method | Modeling Assumptions | Hybrid with Static Model | Static Model Target | Process Model Validation | Process Model Validation Source | Software Tool / Library for Process Model | Modeling Environment for Process Model | Testbed for Application | Testbed Description | Testbed Dynamic Model Target | Testbed Dynamic Modeling Scale | Testbed Model Paradigm | Modeling Method (Testbed) | Modeling Assumptions (Testbed) | Hybrid with Static Model (Testbed) | Static Model Target (Testbed) | Testbed Model Validation | Testbed Validation Source | Software Tool / Library for Testbed | Modeling Environment for Testbed | Hardware / Tools for Deployment | Time Interval (Control or Detection) | Control Variables (CO and EF) | Control Level (CO and EF) | Performance Metrics (Application) | Benchmark | Real-World Implementation | Implementation Type | Process Model-Testbed Gap | Gap Description | Keywords Plus | Addresses | Affiliations | Reprint Addresses | Email Addresses | Times Cited, WoS Core | Times Cited, All Databases | Volume | Issue | Part Number | Special Issue | Start Page | End Page | Article Number
1 | 1 | Data-driven thermal dynamics recognition and multi-objective optimization for building demand response | Xu, RY; Liu, XC; Ruan, GC; Zhang, T; Liu, XH | Xu, Ruoyu; Liu, Xiaochen; Ruan, Guangchun; Zhang, Tao; Liu, Xiaohua | 2026-08-01 | 2025 | http://dx.doi.org/10.1016/j.jobe.2025.112778 | Heating; Ventilation; And air-conditioning (HVAC); Building thermal dynamics; Energy flexibility; Demand response; Machine learning | EF | Journal of Building Engineering | Lack of accurate and computationally efficient thermal dynamics models validated on large multi-zone buildings with diverse HVAC systems for real-time demand response. | 1. Develop a physics-restricted state-space (PRSS) recognition method. 2. Implement a rolling-horizon optimization for demand response. 3. Validate model performance on large-scale buildings. | Subsystem | Building thermal | Component | Gray-Box | Physics-restricted state-space (PRSS), implemented as constrained linear regression incorporating physical laws. | 1. Thermal interactions modeled using state-space with physical constraints (e.g., non-negative heat transfer). 2. Topology modeled as a fully connected graph with resistive and capacitive interpretations. | No | - | Yes | Real data | N/A | MATLAB | Virtual testbed | Same PRSS model | Building thermal | Component | Gray-Box | Physics-restricted state-space (PRSS), implemented as constrained linear regression incorporating physical laws. | 1. Thermal interactions modeled using state-space with physical constraints (e.g., non-negative heat transfer). 2. Topology modeled as a fully connected graph with resistive and capacitive interpretations. | No | - | Yes | Real data | N/A | MATLAB | - | 10min | Chiller plant power, Indoor temperature setpoints | Medium, High | Relative cost (Cr), Relative discomfort (Dr) | N/A | No | Simulation only | No | The process model and testbed are the same | SYSTEMS | [Xu, Ruoyu; Liu, Xiaochen; Zhang, Tao; Liu, Xiaohua] Tsinghua Univ, Sch Architecture, Dept Bldg Sci, Beijing 100084, Peoples R China; [Ruan, Guangchun] MIT, Lab Informat & Decis Syst, Cambridge, MA 02139 USA | Tsinghua University; Massachusetts Institute of Technology (MIT) | Liu, XC; Liu, XH (corresponding author), Tsinghua Univ, Sch Architecture, Dept Bldg Sci, Beijing 100084, Peoples R China. | lxc4@tsinghua.edu.cn; lxh@tsinghua.edu.cn | 0 | 0 | 107 | [5 empty] | 112778
2 | 2 | Hybrid model based predictive control for temperature-humidity regulation in direct expansion air conditioning systems | Xia, YD; Pan, WW; Wang, J; Zhu, CY; Song, MJ | Xia, Yudong; Pan, Wenwen; Wang, Jian; Zhu, Chunyu; Song, Mengjie | 2026-07-01 | 2025 | http://dx.doi.org/10.1016/j.jobe.2025.112560 | Humidity control; Model predictive control; Thermal comfort; Direct expansion air conditioning system; Operational efficiency | CO | Journal of Building Engineering | Most prior MPC applications for DX A/C systems assume ideal insulation and ignore the effects of external weather. They also often rely on empirical (black-box or gray-box) models that cannot fully capture the complex coupling between sensible and latent cooling processes, especially under variable-speed operations. | 1. Develop a hybrid model combining white-box for the cooling coil and gray-box for the room. 2. Design an MPC that simultaneously regulates temperature and humidity. 3. Demonstrate improvements in energy efficiency and comfort. | Subsystem | Building thermal, IAQ | Component | White-Box | Linearized state-space model derived from the hybrid nonlinear model | Linearization around a steady-state operating point | No | - | Yes | Simulated data | quadprog | MATLAB | Virtual testbed | Developed nonlinear hybrid model: White-box: first-principle-based DX coil model; Gray-box: RC (4R3C) thermal model for the room | Building thermal, IAQ, HX | Subsystem | Gray-Box, White-Box | White-box for cooling coil using energy/mass balances; Gray-box 4R3C RC network calibrated via PSO; Moisture balance | Constant subcooling/superheat, insulated ducts | No | - | Yes | Lab | REFPROP | MATLAB | - | 5min | Compressor speed, Supply fan air flow rate | Low, Medium | PMV, Energy consumption | MPC with temperature-only control; Cases with and without humidity control | No | Simulation only | Yes | The process model is a linearized simplification of the nonlinear hybrid model. | FUZZY-LOGIC CONTROLLER; VARIABLE-SPEED; THERMAL-COMFORT; OPERATING CHARACTERISTICS; ENERGY; STABILITY; EEV | [Xia, Yudong; Pan, Wenwen; Wang, Jian] Hangzhou Dianzi Univ, Sch Automat, Sch Artificial Intelligence, Hangzhou, Peoples R China; [Xia, Yudong; Zhu, Chunyu] China Univ Min & Technol, Sch Low Carbon Energy & Power Engn, Xuzhou, Peoples R China; [Song, Mengjie] Beijing Inst Technol, Sch Mech Engn, Dept Energy & Power Engn, Beijing, Peoples R China | Hangzhou Dianzi University; China University of Mining & Technology; Beijing Institute of Technology | Xia, YD (corresponding author), Hangzhou Dianzi Univ, Sch Automat, Sch Artificial Intelligence, Hangzhou, Peoples R China. | ydxia@hdu.edu.cn | 0 | 0 | 105 | [5 empty] | 112560
3 | 3 | HVAC control based on reinforcement learning and fuzzy reasoning: Optimizing HVAC supply air temperature, flow rate, and velocity | Yao, L; Huang, LY; Teo, JC | Yao, Leehter; Huang, Li-Yu; Teo, J. C. | 2026-06-01 | 2025 | http://dx.doi.org/10.1016/j.jobe.2025.112143 | Fuzzy reasoning; Heating; Ventilation and air conditioning (HVAC) control; Predicted mean vote (PMV); Reinforcement learning; PMV | CO | Journal of Building Engineering | Most existing RL-based HVAC control strategies optimize only indoor temperature and often rely on simplified or incomplete representations of occupant comfort. They also overlook joint optimization of HVAC variables like air velocity and airflow rate. | 1. Develop an RL framework that simultaneously optimizes HVAC supply air temperature, flow rate, and velocity. 2. Formulate a mathematical model to compute air velocity from flow rate and duct area. 3. Use action masking to avoid discomfort from high air velocities. 4. Incorporate fuzzy logic into the reward function to better reflect user preferences on PMV and electricity cost. | Subsystem | Building thermal, IAQ | Component | White-Box | Discrete-time, first-order energy and mass balance equation | Linear update dynamics, Constant air density, Simplified PMV and energy cost computation, | Yes | FCU's air flow rate, PMV, Power consumption | No | None | N/A | N/A | Virtual testbed | Same to training environment | Building thermal, IAQ | Component | White-Box | Discrete-time, first-order energy and mass balance equation | Linear update dynamics, Constant air density, Simplified PMV and energy cost computation, | Yes | FCU's air flow rate, PMV, Power consumption | No | None | N/A | N/A | - | 15min | Supply air flow rate and temperature of FCU | Medium | PMV, Energy cost saving | RL baseline controlling only temperature (without fuzzy reasoning or joint optimization) | No | Simulation only | No | The process model (environment) and testbed are the same | ENERGY; VENTILATION; SYSTEMS | [Yao, Leehter; Huang, Li-Yu; Teo, J. C.] Natl Taipei Univ Technol, Dept Elect Engn, Taipei 10608, Taiwan | National Taipei University of Technology | Yao, L (corresponding author), Natl Taipei Univ Technol, Dept Elect Engn, Taipei 10608, Taiwan. | ltyao@ntut.edu.tw | 1 | 1 | 103 | [5 empty] | 112143
4 | 4 | Coupling time-scale reinforcement learning methods for building operational optimization with waste heat | Chen, Z; Xing, T; Wang, Y; Zhuang, YL; Zheng, M; Zhao, QC; Jia, QS | Chen, Zhe; Xing, Tian; Wang, Yu; Zhuang, Yunlin; Zheng, Meng; Zhao, Qianchuan; Jia, Qing-Shan | 2026-08-01 | 2025 | http://dx.doi.org/10.1016/j.apenergy.2025.125851 | Reinforcement learning; Time-scale; Occupant-centric control; HVAC optimization; Waste heat utilization | CO | Applied Energy | Most reinforcement learning (RL)-based HVAC optimization studies lack coordinated control across time-scales (fast local vs. slow global) and often overlook coupling between components like FCUs and heat pumps. They also neglect real-world phenomena like waste heat reuse and realistic occupant behavior. | 1. Propose a coupling time-scale DQN algorithm to coordinate FCU and heat pump control, 2. Develop a high-fidelity simulation testbed with realistic thermal modeling and waste heat utilization, 3.Integrate time-of-use pricing to evaluate energy-aware policies, 4.Compare against conventional RL and OCC methods. | Whole System | TES | Component | White-Box | Discrete-time energy balance for TES | The tank is modeled as having uniform temperature at each timestep, heat is stored and released uniformly throughout the tank. | Yes | Room thermal, pipe network, heat pump | No | None | N/A | Python | Virtual testbed | 7-zone office with FCUs (two types: FP-102, FP-136), one water-source heat pump (WWC 100 H/X), occupancy variations, waste heat recovery tank. Includes weather and price variations. | TES | Component | White-Box | Discrete-time energy balance for TES | The tank is modeled as having uniform temperature at each timestep, heat is stored and released uniformly throughout the tank. | Yes | Room thermal, pipe network, heat pump | No | None | MySQL | Python | - | FCU: 5min; HP: 10min | FCU fan speed (discrete levels: 0–3); Heat pump water temperature setpoint (discretized) | Low, Medium | Indoor temperature, Energy consumption | Separate time-scale DQN; Rule-based occupant-centric control | No | Simulation only | No | The process model (environment) and testbed are the same | MODEL-PREDICTIVE CONTROL; DEMAND-RESPONSE; HVAC CONTROL; SYSTEMS; TEMPERATURE; ENERGY | [Chen, Zhe; Xing, Tian; Wang, Yu; Zhao, Qianchuan; Jia, Qing-Shan] Tsinghua Univ, Ctr Intelligent & Networked Syst, Dept Automat, Beijing 100084, Peoples R China; [Zhuang, Yunlin; Zheng, Meng] Hitachi China Ltd, Res Lab, Beijing 100080, Peoples R China | Tsinghua University | Zhao, QC; Jia, QS (corresponding author), Tsinghua Univ, Ctr Intelligent & Networked Syst, Dept Automat, Beijing 100084, Peoples R China. | chenzhe946@alumni.sjtu.edu.cn; xingt19@tsinghua.org.cn; yuwang@ustb.edu.cn; ylzhuang@hitachi.cn; mzheng@hitachi.cn; zhaoqc@mail.tsinghua.edu.cn; jiaqs@tsinghua.edu.cn | 0 | 0 | 391 | [5 empty] | 125851
5 | 5 | Experimental investigation and scenario-based optimization of energy flexibility in embedded radiant cooling systems | Xie, Y; Li, YX; Cui, HS | Xie, Yun; Li, Yanxue; Cui, Hongshe | MAR | 2025 | http://dx.doi.org/10.1016/j.csite.2025.105835 | Radiant cooling systems; Pre-cooling experiments; Building thermal modeling; Energy flexibility; Model predictive control | EF | Case Studies in Thermal Engineering | Energy flexibility potential of radiant cooling systems is underexplored, particularly in real experimental settings rather than simulations. | 1. Experimentally demonstrate the energy flexibility of radiant cooling panels embedded into the building envelope. 2. Evaluate and compare different dynamic models (ARX, RC, and state-space) using real data. 3. Apply and assess scenario-based MPC strategies for optimizing energy usage, cost, and PV self-consumption. | Subsystem | Building thermal | Component | Black-Box, Gray-Box | Autoregressive exogenous(ARX); 4R3C; State-space model | RC model assumes simplified heat transfer using ODEs. ARX assumes linear relationship with external input delay. State-space assumes linear dynamic structure fitted via subspace identification. | No | - | Yes | Lab | System Identification Toolbox, Quadratic Programming Solver | MATLAB | Lab | Radiant cooling system consists of an air-source heat pump, radiant panels, a fresh air system, a water tank, and a water fluorine heat exchanger | - | - | - | - | - | - | - | - | - | - | - | Thermo recorder TR-7wf, iBEM Lab power management system, K-Type Thermocouple, Local weather stations, Professional Infrared Thermal Imager FLIR T540 | 30min | Electrical power input to the radiant cooling system | Medium | Energy consumption, cost-effectiveness, on-site PV self-consumption, grid import, indoor air temperature | Rule-based control using constant temperature setpoint | Partial | Lab setup | Yes | Model representation limit | MODEL-PREDICTIVE CONTROL; DEMAND RESPONSE; BUILDINGS; STORAGE | [Xie, Yun; Li, Yanxue] Qingdao Univ Technol, Innovat Inst Sustainable Maritime Architecture Res, Qingdao 266033, Peoples R China; [Cui, Hongshe] Qingdao Univ Technol, Sch Environm & Municipal Engn, Qingdao 266033, Shandong, Peoples R China | Qingdao University of Technology; Qingdao University of Technology | Li, YX (corresponding author), Qingdao Univ Technol, Innovat Inst Sustainable Maritime Architecture Res, Qingdao 266033, Peoples R China. | liyanxue@qut.edu.cn | 1 | 1 | 67 | [5 empty] | 105835
6 | 6 | A learning-based model predictive control method for unlocking the potential of building energy flexibility | Zhu, J; Niu, JD; Zhan, SC; Tian, Z; Chong, A; Wang, HL; Zhou, HZ | Zhu, Jie; Niu, Jide; Zhan, Sicheng; Tian, Zhe; Chong, Adrian; Wang, Huilong; Zhou, Haizhu | 2026-03-01 | 2025 | http://dx.doi.org/10.1016/j.enbuild.2025.115299 | Energy flexibility; Model predictive control; Machine learning; Building energy and control simulation; HVAC | EF | Energy and Buildings | Traditional MPC, though effective, is challenging to deploy at scale in real buildings due to its high computational burden and hardware/software resource demands. Moreover, evaluations often overestimate performance by reusing the same model for both optimization and testing, neglecting real-world mismatches. | 1. Propose a learning-based MPC (LBMPC) method using machine learning (CART) to imitate optimal MPC control actions. 2. Build a high-fidelity co-simulation testbed using Spawn of EnergyPlus and Modelica to validate the approach. 3. Evaluate control performance and analyze influences of input features, weather, and model accuracy. | Subsystem | Building thermal | Component | Gray-Box | Second-order RC model, LTI ( linear time-invariant) state-space form | 1. Each thermal zone is modeled independently (decentralized identification). 2. Linear time-invariant dynamics. 3. No inter-zone coupling to improve scalability. | No | - | Yes | Simulated data | System Identification Toolbox, IPOPT, do-mpc, CasADi | MATLAB, Python | Virtual testbed | DOE small office reference building (single-story, 511 m², 5 zones) | VAV system | Subsystem | White-Box | Spawn of EnergyPlus | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | PythonFMU, Modelica Buildings Library, FMI | Python, MATLAB, Modelica, Spawn of EnergyPlus | - | 15min | Zone temperature setpoints, AHU ON/OFF signal | Low, High | Energy cost savings, Peak load reduction, Computational efficiency | Two rule-based control (RBC) strategies: Strategy 1: no pre-cooling; Strategy 2: 2-hour pre-cooling | No | Simulation only | Yes | Model representation limit - The process model (RC) used for training LBMPC is significantly simpler than the white-box testbed | DEMAND-RESPONSE; COMMERCIAL BUILDINGS; CONTROL STRATEGIES; SIMULATION; OPTIMIZATION; PERFORMANCE; IDENTIFICATION; FRAMEWORK; SYSTEMS | [Zhu, Jie; Niu, Jide; Tian, Zhe] Tianjin Univ, Sch Environm Sci & Engn, Tianjin 300072, Peoples R China; [Tian, Zhe] Tianjin Key Lab Bldg Environm & Energy, Tianjin 300072, Peoples R China; [Zhan, Sicheng; Chong, Adrian] Natl Univ Singapore, Coll Design & Engn, Dept Built Environm, 4 Architecture Dr, Singapore 117566, Singapore; [Wang, Huilong] Shenzhen Univ, State Key Lab Intelligent Geotech & Tunnelling, Shenzhen 518060, Peoples R China; [Zhou, Haizhu] China Acad Bldg Res, Beijing 100013, Peoples R China | Tianjin University; National University of Singapore; Shenzhen University | Tian, Z (corresponding author), Tianjin Univ, Sch Environm Sci & Engn, Tianjin 300072, Peoples R China. | tianzhe@tju.edu.cn | 5 | 5 | 330 | [5 empty] | 115299
7 | 7 | Power-controllable variable refrigerant flow system with flexibility value for demand response | Ren, P; Chen, LS; Hui, HX | Ren, Peng; Chen, Lunshu; Hui, Hongxun | 2026-12-30 | 2024 | http://dx.doi.org/10.1016/j.energy.2024.133820 | Demand response; Fuzzy control; Power regulation; Predicted mean vote; Variable refrigerant flow system | EF | Energy | Traditional VRFS control methods based on temperature or compressor state lack precise power controllability and fail to balance power system needs with customer comfort. There is insufficient research on directly power-controllable VRFS systems for demand response (DR). | 1. Propose a power-controllable VRFS capable of directly adjusting compressor power for DR. 2. Introduce a Demand Response (DR) Flexibility Value as a subjective comfort indicator, coordinated with PMV (Predicted Mean Vote). 3. Develop a fuzzy control strategy to balance DR requirements with user comfort. | Subsystem | Building thermal | Component | Gray-Box | Equivalent Thermal Parameter (ETP) model (1R1C) | room envelope as a lumped RC model | Yes | Cooling capacity and the electrical power of the VRFS | Yes | Real data | N/A | Python | Real building | Gree Co. building in Zhuhai: 4 VRFS outdoor units and 20 indoor units; real-time controller; data update every 1 min | - | - | - | - | - | - | - | - | - | - | - | VRFS control center | 1min | VRFS compressor frequency | Low | regulation accuracy, response speed, PMV | No direct comparative baseline; evaluation is based on performance targets and scenarios with DR flexibility values of 0.0, 0.5, 1.0 | Yes | Full-scale real-world deployment | Yes | Model representation limit | AIR-CONDITIONERS; DISPATCH | [Ren, Peng] Gree Elect Appliances Inc Zhuhai, Zhuhai 519070, Guangdong, Peoples R China; [Chen, Lunshu; Hui, Hongxun] Univ Macau, State Key Lab Internet Things Smart City, Macau 999078, Peoples R China; [Chen, Lunshu; Hui, Hongxun] Univ Macau, Dept Elect & Comp Engn, Macau 999078, Peoples R China; [Hui, Hongxun] Sci & Technol Res Inst, Zhuhai 519031, Guangdong, Peoples R China | Gree Electric; University of Macau; University of Macau | Hui, HX (corresponding author), Univ Macau, State Key Lab Internet Things Smart City, Macau 999078, Peoples R China. | hongxunhui@um.edu.mo | 0 | 0 | 313 | [5 empty] | 133820
8 | 8 | Coordinating variable refrigerant flow system for effective demand response in commercial buildings | Wang, D; Zheng, WF; Wang, Z; Huang, YN; Li, S; Li, DD; Li, B; Yan, R | Wang, Dan; Zheng, Wanfu; Wang, Zhe; Huang, Yannan; Li, Shen; Li, Dongdong; Li, Bin; Yan, Rui | 2026-01-01 | 2025 | http://dx.doi.org/10.1016/j.enbuild.2024.115066 | Demand Response; Variable Refrigerant Flow (VRF); Multi-agent coordination; Model Predictive Control; Model uncertainty | EF | Energy and Buildings | Lack of research on how model uncertainty affects the performance of MPC in demand response (DR) coordination of multiple VRF (Variable Refrigerant Flow) systems in commercial buildings. | 1. Develop a virtual testbed to benchmark DR control strategies for VRF systems. 2. Compare MPC, Rule-Based Control (RBC), and Priority Stack-Based Control (PSBC) under varying levels of model uncertainty. 3. Categorize and quantify sources of model uncertainty. 4. Evaluate MPC under linear vs. integer programming formulations. | Subsystem | Building thermal | Component | Gray-Box | Discrete-time state-space model derived from 3R2C with added model uncertainty | Linearly discretized 3R2C model with additive Gaussian uncertainty to represent modeling errors | No | - | Yes | Real data | CVXPY | Python | Virtual testbed | Custom-built virtual testbed consisting of thermal models (3R2C), VRF system abstraction, and TMY3 weather data. | Building thermal | Component | Gray-Box | 3R2C | No noise or uncertainty added | Yes | VRF power model | Yes | Real data | N/A | Python | - | 5min | discrete ON/OFF control signal | Low | energy cost reduction, Load tracking error, computation time | RBC for cost reduction tasks, Priority stack-based control (PSBC) for load tracking tasks | No | Simulation only | No | The process model and testbed are the same | MODEL-PREDICTIVE CONTROL; HVAC SYSTEMS; MPC | [Wang, Dan; Zheng, Wanfu; Wang, Zhe] Hong Kong Univ Sci & Technol, Dept Civil & Environm Engn, Hong Kong, Peoples R China; [Wang, Dan; Zheng, Wanfu; Wang, Zhe] HKUST Shenzhen Hong Kong Collaborat Innovat Res In, Shenzhen, Peoples R China; [Huang, Yannan; Li, Shen; Li, Dongdong; Li, Bin; Yan, Rui] Guangdong Midea Heating & Ventilating Equipment Co, Foshan, Peoples R China | Hong Kong University of Science & Technology | Wang, Z (corresponding author), Hong Kong Univ Sci & Technol, Dept Civil & Environm Engn, Hong Kong, Peoples R China.;Wang, Z (corresponding author), HKUST Shenzhen Hong Kong Collaborat Innovat Res In, Shenzhen, Peoples R China. | cezhewang@ust.hk | 3 | 3 | 326 | [5 empty] | 115066
9 | 9 | Event-driven model-based optimal demand-controlled ventilation for multizone VAV systems: Enhancing energy efficiency and indoor environmental quality | Shi, SR; Miyata, S; Akashi, Y | Shi, Shanrui; Miyata, Shohei; Akashi, Yasunori | 2026-01-01 | 2025 | http://dx.doi.org/10.1016/j.apenergy.2024.124683 | Demand-controlled ventilation; Multizone VAV system; Indoor environmental quality; Energy efficiency; Event-driven optimization | CO | Applied Energy | 1. Lack of integration of building thermal and CO2 in control, affecting temperature prediction and comfort. 2. Absence of direct actuator-level optimization (fan frequency and damper opening). 3. Inadequate modeling of air leakage in systems. 4. High computational burden of conventional time-driven optimization methods. | 1. Propose an event-driven model-based optimal DCV strategy that reduces computational load. 2. Develop a data-driven ANN model for the duct network integrated with building thermal and IAQ models. 3. Enable direct control of actuators (fan frequencies and damper openings). | Subsystem | Building thermal, IAQ | Component | White-Box | RC thermal network model, First-order discrete-time balance model (CO₂ mass balance over Δt) | Simplified heat transfer using thermal resistance/capacitance analogy; Assumes well-mixed air; At each time step, the model computes a steady-state estimate of CO₂ based on current airflow and occupancy. | Yes | VAV duct network, Energy use | Yes | ASHRAE Standard 140 | N/A | Python | Virtual testbed | Python-based simulation of a 6-room multizone VAV system in an experimental building | Building thermal, IAQ | Component | White-Box | RC thermal network model, First-order discrete-time balance model (CO₂ mass balance over Δt) | Simplified heat transfer using thermal resistance/capacitance analogy; Assumes well-mixed air; At each time step, the model computes a steady-state estimate of CO₂ based on current airflow and occupancy. | Yes | VAV duct network, Energy use | Yes | ASHRAE Standard 140 | N/A | Python | - | 10min | Fan frequency, Damper openings | Low | Total IEQ cost (weighted sum of thermal and IAQ discomfort); Energy consumption; Number of optimization runs | Compared against 5 strategies: PI control with return duct CO₂ feedback (PI_R); PI with critical zone CO₂ (PI_CZ); Time-driven setpoint optimization (TD_SP); Time-driven actuator optimization (TD_A); Event-driven setpoint optimization (ED_SP) | No | Simulation only | Yes | Model representation limit - The ANN duct model is trained on a physics-based duct model | CONTROL STRATEGY; HVAC SYSTEMS; AIR | [Shi, Shanrui; Miyata, Shohei; Akashi, Yasunori] Univ Tokyo, Grad Sch Engn, Dept Architecture, Tokyo, Japan | University of Tokyo | Shi, SR (corresponding author), Univ Tokyo, Grad Sch Engn, Dept Architecture, Tokyo, Japan. | shishanrui1910@gmail.com | 3 | 3 | 377 |  | D |  |  |  | 124683
10 | 10 | A novel dynamic predictive control model for variable air volume air conditioning systems using deep learning | Lei, L; Li, ZL | Lei, Lei; Li, Zonglin | 2026-10-15 | 2024 | http://dx.doi.org/10.1016/j.jobe.2024.110314 | Multi-zone building; Indoor temperature and humidity; Deep fuzzy cognitive map; Dynamic predictive control; Air-conditioning system | CO | Journal of Building Engineering | 1. Existing predictive HVAC control systems often suffer from delayed responses and lack real-time adaptability. 2. Many prior works omit detailed modeling of internal heat transfer or oversimplify environmental influences, such as neglecting humidity or radiant loads. 3. Few studies integrate both a physically grounded multi-zone thermal model with a learning-based predictor like DFCM for dynamic predictive control. | 1. Develop a dynamic predictive control framework for indoor temperature and humidity in VAV systems. 2. Integrate an RC-network-based multi-zone building model with a Deep Fuzzy Cognitive Map (DFCM) and PID controller. 3. Validate the approach in a real large commercial building under various weather conditions (sunny, overcast, rainy). | Subsystem | Building thermal, IAQ | Component | White-Box, Black-Box | White-box RC-network two-node wall structure with backward finite difference scheme; Mass balance equations with backward finite difference scheme for humidity model; Black-box Deep fuzzy cognitive map model | Ignore wind influence, humidity transfer through envelopes. Uniform air distribution within zones. Rooms were modeled without occupancy dynamics . | No | - | Yes | Real data | Simulink PLC Coder | N/A | Real building | Three rooms (5m x 3m x 3.4m, clay brick walls) in a 131,000 m² commercial building in Guilin, China. | - | - | - | - | - | - | - | - | - | - | - | SIMATIC S7-1200 programmable controller, Modbus TCP protocol, Si7021-A20-IM digital sensor, Honeywell HSH-M2A sensor, SM206 solar meter | 4min | Opening of the terminal air damper and the chilled water valve in VAV air conditioning system (with constant static pressure control for fan speed) | Low | Indoor temperature and humidity ratio | N/A | Yes | Full-scale real-world deployment | Yes | Model representation limit | HEAT-CONDUCTION; HUMIDITY; TEMPERATURE | [Lei, Lei] Zhejiang Sci Tech Univ, Sch Civil Engn & Architecture, Hangzhou 310018, Peoples R China; [Li, Zonglin] Guilin Univ Elect Technol, Sch Architecture & Transportat Engn, 1 Jinji Rd, Guilin 541004, Peoples R China; [Lei, Lei] Zhejiang Engn Res Ctr Green & Low Carbon Technol B, Hangzhou 310018, Peoples R China | Zhejiang Sci-Tech University; Guilin University of Electronic Technology | Lei, L (corresponding author), Zhejiang Sci Tech Univ, Sch Civil Engn & Architecture, Hangzhou 310018, Peoples R China. | sophia_lei@live.com | 0 | 0 | 95 | [5 empty] | 110314
11 | 11 | Distributed model predictive control of fan coil system | Zhao, AJ; Wei, Y; Quan, W; Xi, JT; Dong, FF | Zhao, Anjun; Wei, Yuan; Quan, Wei; Xi, Jiangtao; Dong, Feifei | 2026-10-01 | 2024 | http://dx.doi.org/10.1016/j.jobe.2024.110028 | Distributed model predictive control; Nash optimization; Beetle antennae search -particle swarm optimization (BAS-PSO) | CO | Journal of Building Engineering | 1. Centralized MPC for fan coil systems suffers from long stabilization time, poor scalability, and heavy computational loads, making it unsuitable for large-scale deployment. 2. Few applications of distributed MPC (DMPC) exist specifically for fan coil units (FCUs), particularly integrating both thermal and hydraulic dynamics. | 1. Develop a fully distributed MPC architecture for multi-zone fan coil systems that optimizes temperature, valve openings, and fan speeds. 2. Propose a hybrid optimization strategy combining Nash equilibrium and BAS-PSO for solving distributed control problems. 3. Validate the method in semi-physical simulations and practical deployments comparing to PID and centralized MPC. | Subsystem | Building thermal | Component | Gray-Box | Discrete-time linear state-space model derived from RC model | Zone-level dynamics represented with low-order differential equations | Yes | Piping network model | Yes | Real data | N/A | N/A | Real building, HIL | Real fan coil units deployed in eight office rooms across two floors in Jianke Building, Xi’an; Semi-physical platform simulates control processes using genuine control process nodes (CPNs), buildings, and fan coils-->98 FCUs | - | - | - | - | - | - | - | - | - | - | - | Genuine control process nodes (CPNs), 10/100Mbps adaptive RJ45 ports | 1h | Valve opening (continuous), Fan gear (discrete: Off, L, M, H) | Low | Indoor temperature, Energy consumption, Response time | Traditional PID, Centralized MPC | Yes | Full-scale real-world deployment | Yes | Model representation limit |  | [Zhao, Anjun; Wei, Yuan; Quan, Wei; Dong, Feifei] Xian Univ Architecture & Technol, Sch Bldg Serv Sci & Engn, Xian 710055, Peoples R China; [Xi, Jiangtao] China Northwest Architecture Design & Res Instite, Xian 744000, Peoples R China | Xi'an University of Architecture & Technology | Quan, W (corresponding author), Xian Univ Architecture & Technol, Sch Bldg Serv Sci & Engn, Xian 710055, Peoples R China. | 3012579463@qq.com | 4 | 4 | 94 | [5 empty] | 110028
12 | 12 | Control-Oriented Modeling, Simulation, and Predictive Control of District Heating Networks | Nigro, L; La Bella, A; Casella, F; Scattolini, R | Nigro, Lorenzo; La Bella, Alessio; Casella, Francesco; Scattolini, Riccardo |  | 2025 | http://dx.doi.org/10.1109/TASE.2024.3460173 | Computational modeling; Mathematical models; Predictive models; Load modeling; District heating; Water heating; Regulators; District heating network; model predictive control; control-oriented model; energy efficiency | CO | IEEE Transactions on Automation Science and Engineering | Lack of: 1. Accurate yet computationally efficient dynamic modeling frameworks for multi-producer district heating networks (DHNs). 2. Control-oriented models suitable for designing predictive control strategies like NMPC that can manage the thermal inertia and operational constraints of DHNs. | 1. Develop a lightweight, high-fidelity DHN simulation model (DHN4Control in Modelica). 2. Create a control-oriented dynamic model via model reduction. 3. Design and evaluate a Nonlinear Model Predictive Control (NMPC) strategy to optimize DHN operations. 4. Validate models on a real-world benchmark: the Thermal Test Facility at RSE (Italy). | Subsystem | District pipe network, TES | Subsystem | White-Box | Reduced-order control-oriented model from the full simulation model | Incompressible water with constant heat capacity, Instantaneous pressure transients, Fixed pipe flow direction in control model | Yes | Thermal loads, Thermal generator | Yes | Simulated data | CasADi | MATLAB | Virtual testbed | Case 1: RSE Thermal Test Facility – a DHN with 13 nodes, multiple branches, 3 generators (gas boiler, heat pump, electric boiler), 1 TES, and 4 loads. Case 2: AROMA Network (roughly 20 times larger than the RSE Test Facility) | District pipe network, TES | Subsystem | White-Box | Nonlinear Partial Differential Equations (PDE), One-dimensional finite-volume method for pip model | 1. Water is assumed incompressible and with constant specific heat; 2. Each pipe is assumed to have rigid metal walls and a constant circular section. 3. Pressure transients are assumed instantaneous, as pressure waves travel in the fluid with the speed of sound, whereas temperature variations travel with the flow velocity. 4. For notational simplicity, the supply and return distribution networks are assumed to have the same topology, as typical in DHNs | Yes | Thermal loads, Thermal generator | Yes | Simulated data | DHN4Control Library | Modelica | - | 30min | Generator supply temperature setpoints, Generator power setpoints, Generator water mass flows, Thermal storage charge/discharge flows | Medium | Operational cost, Energy efficiency, Computational efficiency | Rule-based control | No | Simulation only | Yes | Model representation limit | OPTIMIZATION; SYSTEMS | [Nigro, Lorenzo; La Bella, Alessio; Casella, Francesco; Scattolini, Riccardo] Politecn Milan, Dipartimento Elettron Informaz & Bioingn, I-20133 Milan, Italy; [Nigro, Lorenzo] Ric Sistema Energet RSE SpA, I-20134 Milan, Italy | Polytechnic University of Milan | La Bella, A (corresponding author), Politecn Milan, Dipartimento Elettron Informaz & Bioingn, I-20133 Milan, Italy. | lorenzo.nigro@polimi.it; alessio.labella@polimi.it; francesco.casella@polimi.it; riccardo.scattolini@polimi.it | 0 | 0 | 22 |  |  |  | 7064 | 7079
13 | 13 | Quantifying the potential of load flexibility for building HVAC system using model predictive control strategy | Wang, D; Zheng, WF; Wang, Z; Wu, ZF; Shen, BQ; Tian, SM | Wang, Dan; Zheng, Wanfu; Wang, Zhe; Wu, Zhifu; Shen, Baiqiang; Tian, Shiming | 2026-11-15 | 2024 | http://dx.doi.org/10.1016/j.enbuild.2024.114819 | Building as a battery; Building load flexibility; Demand response; Model Predictive Control | EF | Energy and Buildings | 1. Lack of systematic studies quantifying building load flexibility using consistent metrics (like battery parameters). 2. Few investigations on how internal/external factors (e.g., comfort range, thermal mass, ToU tariffs) influence load flexibility. 3. Existing works primarily use setpoint-based or rule-based control, underutilizing advanced control techniques like MPC. | 1. Develop a methodology to parameterize building load flexibility using battery-like metrics (charging power, storage capacity, round-trip efficiency). 2. Evaluate the impact of multiple parameters (ToU structure, weather, thermal mass, comfort) on flexibility. 3. Compare BaB (building-as-battery) with traditional batteries via techno-economic analysis. | Subsystem | Building thermal | Component | White-Box | First-order RC model (no parameters are learned from data) | Thermal dynamics approximated by first-order RC model. | Yes | Chiller power and cooling output (linear regression model) | No | None | CVXPY | Python | Virtual testbed | Small building testbed modeled in Modelica using Buildings Library | Building thermal | Subsystem | White-Box | Same first-order RC model |  | Yes | Chiller (linear regression model) | No | None | Modelica Buildings Library, PyFMI | Modelica | - | 1h | Chiller power modulation signal (0–1) | Medium | Charging power, Energy storage capacity, Round-trip efficiency, Capital cost, Energy loss | PI controller | No | Simulation only | No | The process model and testbed are the same | COMMERCIAL BUILDINGS; FREQUENCY REGULATION; DEMAND RESPONSE; ENERGY-STORAGE; EFFICIENCY; MPC | [Wang, Dan; Zheng, Wanfu; Wang, Zhe] Hong Kong Univ Sci & Technol, Dept Civil & Environm Engn, Hong Kong, Peoples R China; [Wang, Dan; Zheng, Wanfu; Wang, Zhe] HKUST Shenzhen Hong Kong Collaborat Innovat Res In, Futian, Shenzhen, Peoples R China; [Wu, Zhifu; Shen, Baiqiang] State Grid Zhejiang Elect Power Co Ltd, Quzhou, Zhejiang, Peoples R China; [Tian, Shiming] China Elect Power Res Inst, Beijing, Peoples R China | Hong Kong University of Science & Technology; State Grid Corporation of China; State Grid Corporation of China; China Electric Power Research Institute (CEPRI) | Wang, Z (corresponding author), HKUST Shenzhen Hong Kong Collaborat Innovat Res In, Futian, Shenzhen, Peoples R China. | cezhewang@ust.hk | 2 | 2 | 323 | [5 empty] | 114819
14 | 14 | Optimal control strategy for building HVAC systems: Satisfying flexible demand response with different value-based selection | Sun, YF; Shen, Q; Liu, XH; Zhang, L; Li, X; Zhang, T; Lin, MS | Sun, Yifu; Shen, Qi; Liu, Xiaohua; Zhang, Lei; Li, Xin; Zhang, Tao; Lin, Meishun | 2026-11-15 | 2024 | http://dx.doi.org/10.1016/j.enbuild.2024.114823 | Demand response; Flexibility; Optimal control; HVAC; Load demand; Space demand; Carbon emissions | EF | Energy and Buildings | 1. Most previous research relies heavily on simulation-based studies lacking real-world validation. 2. Prior studies rarely consider fluctuating carbon emission factors—an increasingly critical factor in China’s carbon neutrality goals. 3. Limited granularity in flexibility modeling (e.g., room-specific control difficulty is often overlooked). | 1. To propose a hierarchical control framework for HVAC systems integrating: Load demand assignment, Space-level demand interpretation, Real-time control; 2. To optimize HVAC operation with value-based objectives: minimizing energy, cost, or carbon emissions. 3. To demonstrate the approach in a real commercial building. | Whole System | Building thermal | Component | Gray-Box, Black-Box | RC model for building thermal, LSTM for single room temperature | Fixed ventilation rate during training | Yes | Chiller and terminal unit fan power | Yes | Real data | N/A | N/A | Real building | Commercial plaza in Beijing | - | - | - | - | - | - | - | - | - | - | - | N/A | 15min | Indoor temperature setpoints (space-wise), Start and stop times for room cooling | High | Indoor temperature, Electricity consumption, Electricity cost, Carbon emissions | Energy-consumption optimization only | Yes | Full-scale real-world deployment | Yes | Model representation limit | TIME-SERIES; FLEXIBILITY | [Sun, Yifu; Shen, Qi; Zhang, Lei; Li, Xin; Lin, Meishun] Persagy Technol Co Ltd, Beijing 100096, Peoples R China; [Liu, Xiaohua; Zhang, Tao] Tsinghua Univ, Dept Bldg Sci, Beijing 100084, Peoples R China | Tsinghua University | Sun, YF (corresponding author), Persagy Technol Co Ltd, Beijing 100096, Peoples R China. | sunyifu@yushu.biz | 6 | 6 | 323 | [5 empty] | 114823
15 | 15 | Deep reinforcement learning control for co-optimizing energy consumption, thermal comfort, and indoor air quality in an office building | Guo, FZ; Ham, SW; Kim, D; Moon, HJ | Guo, Fangzhou; Ham, Sang woo; Kim, Donghun; Moon, Hyeun Jun | 2026-01-01 | 2025 | http://dx.doi.org/10.1016/j.apenergy.2024.124467 | Deep reinforcement learning; Deep deterministic policy gradient; Smart building; Air conditioning; Energy efficiency; Thermal comfort; Indoor air quality | CO | Applied Energy | Existing DRL studies rarely address full-scale central HVAC systems that control both water and air loops, and even fewer co-optimize energy consumption, thermal comfort, CO₂, and PM2.5 levels. Moreover, challenges include lack of suitable simulators and difficulties resolving conflicting objectives (e.g., outdoor air improves CO₂ but may worsen PM2.5). | 1. Develop a DRL algorithm (DDPG) for central HVAC systems to co-optimize energy, thermal comfort, CO₂, and PM2.5. 2. Build a calibrated hybrid simulation environment. 3. Compare DRL performance against MPC and rule-based baselines. | Whole System | ASHP, AHU, Building thermal, IAQ | Whole System | Gray-Box, White-Box | Gray-box: 2R2C; White-box: Modelica-based HVAC system model, ODE based on moisture/CO2/PM2.5 mass balance | Uniform zone conditions. | No | - | Yes | Real data | PyFMI, Modelica Buildings Library | Modelica, Python | Virtual testbed | Model based on FLEXLAB test cell (56 m² office mock-up with 6 cubicles, chiller, AHU, air purifier). | ASHP, AHU, Building thermal, IAQ | Whole System | White-Box, Gray-Box | Gray-box: 2R2C; White-box: HVAC system model, ODE based on moisture/CO2/PM2.5 mass balance | Uniform zone conditions. | No | - | Yes | Real data | PyFMI, Modelica Buildings Library | Modelica, Python | - | 15min | Chilled water supply temperature, Outdoor air damper opening, Supply air fan speed, Air purifier ON/OFF | Low, Medium | Energy consumption, Thermal comfort (zone temperature, RH, psychrometric zone, PPD), Indoor CO₂ concentration, Indoor PM2.5 concentration | Rule-based controller, Model Predictive Control | No | Simulation only | No | The process model (environment) and testbed are the same | MODELS | [Guo, Fangzhou; Ham, Sang woo; Kim, Donghun] Lawrence Berkeley Natl Lab, Berkeley, CA 94720 USA; [Moon, Hyeun Jun] Dankook Univ, Dept Architectural Engn, Yongin, South Korea | United States Department of Energy (DOE); Lawrence Berkeley National Laboratory; Dankook University | Guo, FZ (corresponding author), Lawrence Berkeley Natl Lab, Berkeley, CA 94720 USA. | fzguo@lbl.gov | 7 | 7 | 377 |  | A |  |  |  | 124467
16 | 16 | Offset-Free Koopman Model Predictive Control of Thermal Comfort Regulation for a Variable Refrigerant Flow-Dedicated Outdoor Air System-Combined System | Pan, C; Li, YY; Dong, LJ | Pan, Chao; Li, Yaoyu; Dong, Liujia | 2026-09-01 | 2024 | http://dx.doi.org/10.1115/1.4065144 | Koopman model predictive control; offset-free model predictive control; model reduction; variable refrigerant low system; dedicated outdoor air system; functional mockup interface co-simulation | CO | Journal of Dynamic Systems, Measurement, and Control | Most VRF control strategies overlook humidity regulation, which is crucial for thermal comfort. Coordinating VRF and DOAS systems is complex due to mixed latent and sensible loads, and model-based control strategies suffer from high computational costs and sensitivity to model errors. | To develop an offset-free Koopman MPC strategy for thermal comfort regulation (temperature + humidity) in a VRF-DOAS combined system, enhancing robustness and reducing computational burden via reduced-order Koopman modeling. | Whole System | Building thermal, IAQ | Component | Black-Box | State-space formulation of reduced-Koopman model | Lumped air volume with ideal mixing | No | - | Yes | Simulated data | CVXPY, Gurobi, MORLAB | Python | Virtual testbed | Full VRF-DOAS system simulated in Modelica | VRF-DOAS system | Whole System | White-Box | First-principles physics-based modeling in Modelica | Symmetric and identical zones | No | - | No | None | TIL Library, TIL Media Library, Modelica Buildings Library, FMPy | Modelica | - | 100s | DOAS compressor speed, VRF compressor speed, Outdoor air ratio (OAR), VRF IDU fan speed | Low | Indoor temperature and humidity ratio, Power consumption, Computation time | Baseline Linear MPC, Offset-Free Linear MPC | No | Simulation only | Yes | Model representation limit; Omit the full physics of the VRF-DOAS system | CONDITIONING SYSTEM; ENERGY; TEMPERATURE; ALGORITHM | [Pan, Chao; Li, Yaoyu] Univ Texas Dallas, Dept Mech Engn, 800 W Campbell Rd, Richardson, TX 75080 USA; [Dong, Liujia] Carrier Global Corp, 1203 Kinne St, East Syracuse, NY 13057 USA | University of Texas System; University of Texas Dallas | Li, YY (corresponding author), Univ Texas Dallas, Dept Mech Engn, 800 W Campbell Rd, Richardson, TX 75080 USA. | chao.pan@utdallas.edu; yaoyu.li@utdallas.edu; liujiadong0826@gmail.com | 1 | 1 | 146 | 5 |  |  |  |  | 51002
17 | 17 | Dynamic modeling and defrost optimization for air source heat pumps: A deep learning and autoregression approach | Chen, L; Wang, WP; Yang, XY; Liu, HC; Ou, RH | Chen, Lei; Wang, Wenpeng; Yang, Xueyuan; Liu, Hecheng; Ou, Ruhao | 2026-11-01 | 2024 | http://dx.doi.org/10.1016/j.enbuild.2024.114689 | Air source heat pump; Defrosting control; Dynamic model; Transfer learning; Deep learning | CO | Energy and Buildings | There is a lack of dynamic data-driven modeling approaches for air source heat pumps (ASHPs), particularly for capturing performance under frosting and defrosting conditions. Existing methods are either steady-state or fully physics-based, which face adaptability and complexity challenges. | 1. Develop dynamic ASHP models using deep learning (primarily TCN) for heating capacity and fin temperature. 2. Incorporate feature encoding (control and time) to enhance model prediction. 3. Use transfer learning to improve generalization across different environmental conditions. 3. Propose and evaluate a Heating Capacity Degradation (HCD)-based defrost control strategy for energy efficiency improvement. | Subsystem | ASHP | Subsystem | Black-Box | Temporal Convolutional Network (TCN) | N/A | No | - | Yes | Lab | N/A | N/A | Virtual testbed | ASHP with indoor and outdoor units | ASHP | Subsystem | Black-Box | Temporal Convolutional Network (TCN) | N/A | No | - | Yes | Lab | N/A | N/A | - | 5s | Operating Mode: Compressor off, Heating mode, Defrosting mode | Low | Average Heating Capacity, Heating capacity loss | Compared to Time-Temperature (T-T) baseline defrost control; Other models: Transformer, LSTM, LightGBM | No | Simulation only | No | The process model (environment) and testbed are the same | FROST GROWTH; START-TIME; PERFORMANCE; SYSTEM | [Chen, Lei; Wang, Wenpeng; Yang, Xueyuan; Liu, Hecheng; Ou, Ruhao] Midea Corp Res Ctr, Foshan 528311, Guangdong, Peoples R China | Midea Corporate Research Center | Chen, L (corresponding author), Midea Corp Res Ctr, Foshan 528311, Guangdong, Peoples R China. | chenlei183@midea.com; wenpeng.wang@midea.com; yangxy44@midea.com; hecheng.liu@midea.com; ruhao.ou@midea.com | 2 | 2 | 322 | [5 empty] | 114689
18 | 18 | Refrigerant leakage detection in building heat pump systems based on dynamic modeling and sensitivity parameters | Zhao, YF; Yang, Z; Hou, ZN; Zhang, SP; Hu, YS; Shu, Y | Zhao, Yanfeng; Yang, Zhao; Hou, Zhaoning; Zhang, Shuping; Hu, Yansong; Shu, Yue | 2026-10-15 | 2024 | http://dx.doi.org/10.1016/j.enbuild.2024.114669 | Water-water heat pump system; Refrigerant leakage; Refrigerant Charge; Fault detection; COP and capacity | FDD | Energy and Buildings | Existing refrigerant charge and leakage detection methods rely heavily on steady-state models and single-parameter analysis, overlooking the dynamic behavior of multi-parameter interactions in building heat pump systems. | 1. Develop a dynamic modeling simulation platform for WWHP systems. 2. Analyze sensitivity of system parameters under varying charge and leakage conditions. 3. Validate the model through experimental data. 4. Create a Python-based charge and leakage detection tool based on the model. | Component | WSHP | Component | White-Box | Physics-based modular modeling using mass, energy, momentum conservation + MBWR state equations. | 1D incompressible fluid flow; Compressor return fully gaseous; Neglects oil return temperature effect; Two-phase fluid in thermodynamic equilibrium (homogeneous) | No | - | Yes | Lab | Refprop, Dynamic Link Library | AMESim | Lab | WWHP setup with scroll compressor (R134a), plate heat exchangers, Carel electronic expansion valve, accumulator, sensors, and a data acquisition system. | - | - | - | - | - | - | - | - | - | - | - | PLC Step7 V4.0, KingView 6.52, YDFLOW 2.0 Software, Siemens S7 − 200 | 30s | - | - | Detection accuracy and time | None | Partial | Lab setup | Yes | Model representation limit | PRESSURE-DROP; GENERAL CORRELATION; CHARGE; PERFORMANCE; FLOW; CONDENSATION; IMPACT; FAULTS; STORAGE; SINGLE | [Zhao, Yanfeng; Yang, Zhao; Hou, Zhaoning; Zhang, Shuping; Hu, Yansong] Tianjin Univ, State Key Lab Engines, Tianjin 300350, Peoples R China; [Shu, Yue] Hefei Gen Machinery Res Inst, State Key Lab High end Compressor & Syst Technol, Hefei 230031, Anhui, Peoples R China | Tianjin University | Yang, Z (corresponding author), Tianjin Univ, State Key Lab Engines, Tianjin 300350, Peoples R China. | zhaoyang@tju.edu.cn | 2 | 2 | 321 | [5 empty] | 114669
19 | 19 | A bi-level real-time optimal control strategy for thermal coupled multi-zone dedicated outside air system-assisted HVAC systems | Liu, YT; Cui, C | Liu, Yuntao; Cui, Can | 2026-10-15 | 2024 | http://dx.doi.org/10.1016/j.energy.2024.132343 | Dedicated outside air system; Multi-zone HVAC system; Thermal coupling; Optimal control; Deep reinforcement learning; Augmented genetic algorithm | CO | Energy | 1. Existing DRL-based HVAC control strategies are largely focused on single-zone systems and fail to address challenges in thermally coupled multi-zone systems. 2. There is a lack of effective real-time optimal control methods for multi-zone DOAS-assisted HVAC systems that simultaneously manage IAQ, thermal comfort, and energy efficiency under thermal coupling. 3. Traditional optimization methods are heavily model-dependent and struggle with convergence and generalization in complex environments. | 1. Propose a bi-level real-time optimal control strategy for thermally coupled multi-zone DOAS-assisted HVAC systems. 2. Use SAC-LRS (Soft Actor-Critic with Lyapunov-based reward shaping) at the upper level for IAQ optimization and an Augmented Genetic Algorithm (AGA) at the lower level for thermal comfort control. 3. Realize unidirectional decoupling between IAQ and thermal comfort control to reduce model dependence and improve optimization effectiveness. 4. Validate performance under different climate and occupancy scenarios. | Whole System | Building thermal, IAQ | Component | White-Box | First-principle energy balance equations for temperature and mass balance for CO₂ | Uniform air mixture in zones. Steady-state wall/window heat transfer. | Yes | Energy consumption models of supply fan and FCU | No | None | N/A | MATLAB | Virtual testbed | 5-zone office setup, DOAS and FCU systems with realistic topology and control constraints | Building thermal, IAQ | Component | White-Box | First-principle energy balance equations for temperature and mass balance for CO₂ | Uniform air mixture in zones. Steady-state wall/window heat transfer. | Yes | Energy consumption model of supply fan and FCU | No | None | N/A | MATLAB | - | 1h | Supply airflow rate (from DOAS), FCU supply power (zone-level) | Medium | Indoor temperature, Indoor CO₂ concentration, Energy consumption, Electricity cost | PID-based control; Occupancy-based control (supply airflow rate based on zone area and maximum occupant capacity ) | No | Simulation only | No | The process model (environment) and testbed are the same | OPTIMIZATION; ALGORITHM; MODEL | [Liu, Yuntao; Cui, Can] Ocean Univ China, Coll Engn, 238 Songling Rd, Qingdao, Peoples R China | Ocean University of China | Cui, C (corresponding author), Ocean Univ China, Coll Engn, 238 Songling Rd, Qingdao, Peoples R China. | cuican@ouc.edu.cn | 1 | 1 | 306 | [5 empty] | 132343
20 | 20 | Ventilation and temperature control for energy-efficient and healthy buildings: A differentiable PDE approach | Bian, YX; Fu, XH; Gupta, RK; Shi, YY | Bian, Yuexin; Fu, Xiaohan; Gupta, Rajesh K.; Shi, Yuanyuan | 2026-10-15 | 2024 | http://dx.doi.org/10.1016/j.apenergy.2024.123477 | Energy-efficient buildings; Data-driven control; Heating ventilation and air conditioning; (HVAC) system; Indoor air quality; Control of partial differential equations | CO | Applied Energy | Traditional HVAC control strategies either oversimplify the dynamics (e.g., using ODEs that neglect spatial effects) or are impractical for control (e.g., CFD models). There's a lack of accurate, tractable models for real-time airflow and thermal control that also guarantee energy savings and air quality. | To propose a PDE-based learning and control framework for HVAC systems that: 1. Accurately models airflow, temperature, and CO₂ using Navier–Stokes and convection–diffusion PDEs; 2. Learns model parameters from data; 3. Optimizes HVAC control (airflow rate, supply temperature) under health and comfort constraints using PDE-constrained optimization. | Subsystem | Indoor temperature field, Indoor airflow field, Indoor CO2 field | Component | White-Box | Navier–Stokes for airflow; Convection–diffusion PDEs for temperature and CO₂ | incompressible flow, Insulated walls | No | - | Yes | Real data | PhiFlow, PyTorch | Python | Virtual testbed | 2D simulated office space (4.2m x 2.7m) with ceiling-mounted supply/return vents | Indoor temperature field, Indoor airflow field, Indoor CO2 field | Component | White-Box | Navier–Stokes for airflow; Convection–diffusion PDEs for temperature and CO₂ | incompressible flow, Insulated walls, constant ambient temperature on window wall | No | - | Yes | Real data | N/A | Python | - | 1min | Supply airflow rate, supply air temperature | Medium | Energy consumption, Violations of CO₂ and temperature constraints | Maximum airflow policy, Minimum airflow policy, MPC with ODE models, RL (PPO-based) | No | Simulation only | No | The process model and testbed are the same | SPREAD | [Bian, Yuexin; Shi, Yuanyuan] Univ Calif San Diego, Dept Elect & Comp Engn, La Jolla, CA 92037 USA; [Fu, Xiaohan; Gupta, Rajesh K.] Univ Calif San Diego, Dept Comp Sci & Engn, La Jolla, CA 92037 USA | University of California System; University of California San Diego; University of California System; University of California San Diego | Shi, YY (corresponding author), Univ Calif San Diego, Dept Elect & Comp Engn, La Jolla, CA 92037 USA. | yyshi@eng.ucsd.edu | 2 | 2 | 372 | [5 empty] | 123477
21 | 21 | Multi-Zone HVAC Control With Model-Based Deep Reinforcement Learning | Ding, XZ; Cerpa, A; Du, W | Ding, Xianzhong; Cerpa, Alberto; Du, Wan | 2024 JUN 14 | 2024 | http://dx.doi.org/10.1109/TASE.2024.3410951 | HVAC; Buildings; Heuristic algorithms; Adaptation models; Neural networks; Predictive models; Optimization; HVAC control; model-based deep reinforcement learning; model predictive control; energy efficiency; optimal control | CO | IEEE Transactions on Automation Science and Engineering | Model-Free Reinforcement Learning (MFRL) for HVAC control, while effective, requires massive training data and has limited data efficiency. Existing Model-Based RL (MBRL) solutions improve sample efficiency but struggle with control performance, especially in multi-zone settings due to model uncertainty and suboptimal action sampling. | To develop a new MBRL-based HVAC control method—MB2C—that combines high sample efficiency with strong control performance. It introduces: 1. Environment-conditioned ensemble neural networks for dynamic modeling. 2. Model Predictive Path Integral (MPPI) for action selection in high-dimensional multi-zone settings. | Subsystem | Indoor air temperature, IAQ | Subsystem | Black-Box | Ensemble of environment-conditioned neural networks (3-layer fully-connected) | N/A | No | - | Yes | Simulated data | TensorFlow | Python | Virtual testbed | Single-floor office building with 5 thermal zones | Building thermal | Component | White-Box | EnergyPlus physics-based simulation | N/A | Yes | VAV system | No | None | BCVTB | EnergyPlus | - | 15min | Zone heating and cooling temperature setpoints (2 per zone × 5 zones = 10 variables) | High | Energy consumption, PMV, Convergence time | Rule-based method, Model-free DRL (PPO), Model-based DRL with random shooting (RS) | No | Simulation only | Yes | Model representation limit | BUILDINGS; DYNAMICS; IOT | [Ding, Xianzhong; Cerpa, Alberto; Du, Wan] Univ Calif Merced, Dept Comp Sci & Engn, Merced, CA 95343 USA | University of California System; University of California Merced | Du, W (corresponding author), Univ Calif Merced, Dept Comp Sci & Engn, Merced, CA 95343 USA. | xding5@ucmerced.edu; acerpa@ucmerced.edu; wdu3@ucmerced.edu | 4 | 4
22 | 22 | Real building implementation of a deep reinforcement learning controller to enhance energy efficiency and indoor temperature control | Silvestri, A; Coraci, D; Brandi, S; Capozzoli, A; Borkowski, E; Köhler, J; Wu, D; Zeilinger, MN; Schlueter, A | Silvestri, Alberto; Coraci, Davide; Brandi, Silvio; Capozzoli, Alfonso; Borkowski, Esther; Kohler, Johannes; Wu, Duan; Zeilinger, Melanie N.; Schlueter, Arno | 2026-08-15 | 2024 | http://dx.doi.org/10.1016/j.apenergy.2024.123447 | Deep reinforcement learning; Real implementation; Building energy management; HVAC control; Energy efficiency | CO | Applied Energy | Most DRL applications in HVAC control have been validated only in simulation or lab testbeds. Real-world implementation remains scarce, especially for low-level control in Thermally Activated Building Systems (TABS). Benchmarking methods for real DRL deployment are lacking. | 1. Demonstrate real-world DRL deployment as a low-level controller managing TABS valve actuation. 2. Compare performance against MPC, PI, and RBC in simulation. 3. Validate DRL in a real building and introduce benchmarking methodology. 4. Propose an interoperable, sensor-light deployment approach. | Subsystem | Building thermal | Component | Gray-Box | RC model (Resistance-Capacitance networks with 1st to 3rd order configurations) | Lumped air volume with ideal mixing | No | - | Yes | Real data | OpenAI Gym | Python | Real building | HiLo unit in NEST (EMPA, Switzerland) — a living lab office space (22.94 m²) with integrated TABS, Hybrid Variable Refrigerant Flow (HVRF), and mechanical ventilation. Focused only on TABS with existing sensor infrastructure (indoor/outdoor temperature, solar radiation, occupancy). | - | - | - | - | - | - | - | - | - | - | - | PLC, Modbus RTU RS485, Standard analog/digital signals (0–10 V, 4–20 mA, PT1000, DI/DO), OPC-UA protocol, Open DataBase Connectivity (ODBC), REST API, Gateway | 5min | TABS valve opening percentage | Low | Indoor temperature, Energy consumption | Simulated: 3 RBCs, 2 PI controllers, ideal MPC; Real: Best-performing RBC (RBC3) | Yes | Full-scale real-world deployment | Yes | The DRL agent was trained on a simplified RC model that does not fully represent real-world thermal dynamics, particularly high-frequency variations or unmodeled internal gains. However, it demonstrated robustness and adaptability in deployment. | MANAGEMENT; SIMULATION; FRAMEWORK; SYSTEMS; NEST | [Silvestri, Alberto; Borkowski, Esther; Schlueter, Arno] Swiss Fed Inst Technol, Architecture & Bldg Syst, Zurich, Switzerland; [Coraci, Davide; Brandi, Silvio; Capozzoli, Alfonso] Politecn Torino, BAEDA Lab, Dept Energy, TEBE Res Grp, Turin, Italy; [Kohler, Johannes; Zeilinger, Melanie N.] Swiss Fed Inst Technol, Inst Dynam Syst & Control, Zurich, Switzerland; [Wu, Duan] Mitsubishi Elect R&D Ctr Europe BV, Livingston, Scotland | Swiss Federal Institutes of Technology Domain; ETH Zurich; Polytechnic University of Turin; Swiss Federal Institutes of Technology Domain; ETH Zurich | Silvestri, A (corresponding author), Swiss Fed Inst Technol, Architecture & Bldg Syst, Zurich, Switzerland. | silvestri@arch.ethz.ch | 20 | 20 | 368 | [5 empty] | 123447
23 | 23 | Model predictive control for thermal comfort and energy optimization of an air handling unit system in airport terminals using occupant feedback | Ma, K; Wang, D; Sun, YY; Wang, W; Gu, XL | Ma, Kai; Wang, Dan; Sun, Yuying; Wang, Wei; Gu, Xianliang | MAY | 2024 | http://dx.doi.org/10.1016/j.seta.2024.103790 | Dynamic occupant flow; Baggage claim hall; Air conditioning system; Model predictive control | CO | Sustainable Energy Technologies and Assessments | Existing MPC strategies are rarely applied to large-scale transportation buildings like airport terminals due to the complex and dynamic nature of occupant flows. Feedback-based HVAC systems suffer from regulation lag, leading to discomfort and energy waste | 1. Propose a dynamic occupant-based MPC (OBMPC) to mitigate regulation lag. 2. Integrate mathematical and agent-based modeling (AnyLogic) to predict dynamic occupant flow. 3. Evaluate OBMPC performance vs. Rule-Based Control (RBC) over a full cooling season. | Subsystem | Building thermal | Component | Black-Box | Autoregressive model with exogenous inputs (ARX) | Lumped air volume with ideal mixing | Yes | Energy system model | Yes | Simulated data | N/A | Python | Virtual testbed | Simulated baggage claim hall of an airport in Beijing using Modelica | VAV system, Chiller plant | Whole System | White-Box | Physical modeling in Modelica using Buildings Library | Uniform indoor air mixture | No | - | No | None | Modelica Buildings Library | Modelica | - | 20min | Air supply temperature, Air supply volume | Medium | Indoor temperature, Energy consumption, Regulation lag (time delay) | Rule-Based Control (RBC) strategy with PI control | No | Simulation only | Yes | Model representation limit | BUILDINGS; IMPLEMENTATION; TIME | [Ma, Kai; Sun, Yuying; Wang, Wei] Beijing Univ Technol, Beijing Key Lab Green Built Environm & Energy Effi, Beijing 100124, Peoples R China; [Wang, Dan] Hong Kong Univ Sci & Technol, Dept Civil & Environm Engn, Hong Kong, Peoples R China; [Wang, Wei] Beijing Inst Petrochem Technol, Informat & Safety Engn, Beijing 102617, Peoples R China; [Gu, Xianliang] Beijing Inst Architectural Design, Beijing 100045, Peoples R China | Beijing University of Technology; Hong Kong University of Science & Technology | Wang, W (corresponding author), Beijing Univ Technol, Beijing Key Lab Green Built Environm & Energy Effi, Beijing 100124, Peoples R China.;Wang, D (corresponding author), Hong Kong Univ Sci & Technol, Dept Civil & Environm Engn, Hong Kong, Peoples R China. | danwang@ust.hk; mrwangwei@bjut.edu.cn | 6 | 6 | 65 | [5 empty] | 103790
24 | 24 | Heuristic model predictive control implementation to activate energy flexibility in a fully electric school building | Morovat, N; Athienitis, AK; Candanedo, JA; Nouanegue, HF | Morovat, Navid; Athienitis, Andreas K.; Candanedo, Jose Agustin; Nouanegue, Herve Frank | 2026-06-01 | 2024 | http://dx.doi.org/10.1016/j.energy.2024.131126 | Energy flexibility; Model predictive control; Building demand response; School buildings | EF | Energy | Most prior MPC studies focus on cooling-dominated regions. There is limited research on activating energy flexibility in cold-climate, fully electric buildings like schools that experience grid stress during winter peaks. | To develop and demonstrate a heuristic MPC strategy using simplified grey-box models and weather-based clustering to activate energy flexibility in an electric school. The aim is to reduce peak demand and electricity costs while maintaining thermal comfort and allowing replicability in similar buildings. | Whole System | Building thermal | Component | Gray-Box | RC thermal networks (3rd-order for convective zones, 4th-order for radiant floor zones). | Lumped air volume with ideal mixing | No | - | Yes | Real data | CVXPY, ECOS, SLSQP | Python | Real building, Virtual testbed | A 5200 m² fully electric elementary school near Montreal, Canada | Building thermal | Component | Gray-Box | RC thermal networks (3rd-order for convective zones, 4th-order for radiant floor zones). | Lumped air volume with ideal mixing | No | - | Yes | Real data | N/A | Python | BACnet, Weather data: SIMEB website, CanMETEO® program | 15min | Setpoint temperature for zone heating | High | Indoor temperature, Peak load reduction, Building Energy Flexibility Index, Electricity cost savings | Comparison with reference classrooms using default PI-controlled thermostats. | Yes | Full-scale real-world deployment | Yes, No | Model representation limit | DEMAND FLEXIBILITY; HEATING-SYSTEMS; STORAGE | [Morovat, Navid; Athienitis, Andreas K.] Concordia Univ, Ctr Zero Energy Bldg Studies, Montreal, PQ, Canada; [Candanedo, Jose Agustin] Univ Sherbrooke, Dept Civil & Bldg Engn, Sherbrooke, PQ, Canada; [Nouanegue, Herve Frank] Hydroquebec Res Inst, Lab Energy Technol, Shawinigan, PQ, Canada | Concordia University - Canada; University of Sherbrooke | Morovat, N (corresponding author), Concordia Univ, Ctr Zero Energy Bldg Studies, Montreal, PQ, Canada. | n_morova@encs.concordia.ca; andreask.athienitis@concordia.ca; jose.candanedo@usherbrooke.ca; nouanegue.hervefrank@hydroquebec.com | 15 | 15 | 296 | [5 empty] | 131126
25 | 25 | Model-based optimal control strategy for multizone VAV air-conditioning systems for neutralizing room pressure and minimizing fan energy consumption | Shi, SR; Miyata, S; Akashi, Y; Momota, M; Sawachi, T; Gao, Y | Shi, Shanrui; Miyata, Shohei; Akashi, Yasunori; Momota, Masashi; Sawachi, Takao; Gao, Yuan | 2026-05-15 | 2024 | http://dx.doi.org/10.1016/j.buildenv.2024.111464 | Model-based optimal control; Multizone VAV system; Room pressure; Indoor air temperature; Energy efficiency; Multiobjective optimization | CO | Building and Environment | 1. Existing VAV control strategies focus predominantly on the supply side, neglecting the return side. They fail to address room pressure imbalances and air leakage, which compromise energy efficiency and indoor air quality. 2. Combining static pressure reset (SPR) with airflow tracking cannot ensure room pressure neutralization in multizone VAV systems. 3. Existing SPR methods rely on localized heuristics and historical states, resulting in suboptimal joint optimization. | 1. Develop a model-based optimal control strategy for multizone VAV systems. 2. Simultaneously regulate indoor air temperature, room pressure, and fan energy consumption. 3.Formulate and implement a multiobjective optimization framework using validated physical models and SAPSO (Simulated Annealing Particle Swarm Optimization). | Subsystem | Building thermal | Component | White-Box | 5R1C RC thermal model | Lumped air volume with ideal mixing | Yes | VAV duct network, Energy use | No | None | N/A | Python | Virtual testbed | A six-zone experimental VAV system in a lab building in Ibaraki Prefecture, Japan | Building thermal | Component | White-Box | 5R1C RC thermal model | Lumped air volume with ideal mixing | Yes | VAV duct network, Energy use | No | None | N/A | Python | - | 30min | Supply and exhaust fan frequency, Damper openings for both SA and RA ducts | Low | Indoor temperature, Room pressure, Air leakage, Fan energy consumption, Total system energy consumption | PID-based control | No | Simulation only | No | The process model and testbed are the same | OPTIMIZATION ALGORITHM; VENTILATION SYSTEM; PREDICTIVE CONTROL | [Shi, Shanrui; Miyata, Shohei; Akashi, Yasunori] Univ Tokyo, Grad Sch Engn, Dept Architecture, Tokyo, Japan; [Momota, Masashi] Tokyo Denki Univ, Tokyo, Japan; [Sawachi, Takao] Bldg Res Inst, Ibaraki, Japan; [Gao, Yuan] Kyushu Univ, Int Inst Carbon Neutral Energy Res WPI I2CNER, Ctr Energy Syst Design CESD, Fukuoka, Japan | University of Tokyo; Tokyo Denki University; Kyushu University | Shi, SR (corresponding author), Univ Tokyo, Grad Sch Engn, Dept Architecture, Tokyo, Japan. | shishanrui@g.ecc.u-tokyo.ac.jp | 6 | 6 | 256 | [5 empty] | 111464
26 | 26 | Data-driven approach for the detection of faults in district heating networks | Losi, E; Manservigi, L; Spina, PR; Venturini, M | Losi, Enzo; Manservigi, Lucrezia; Spina, Pier Ruggero; Venturini, Mauro | JUN | 2024 | http://dx.doi.org/10.1016/j.segan.2024.101355 | District heating networks; Diagnostics; Fault detection and identification; Neural networks | FDD | Sustainable Energy, Grids and Networks | Most existing diagnostic methodologies focus on detecting only one fault type (e.g., leakage or heat loss) at a time and often rely on physics-based models requiring detailed system knowledge. There is a lack of comprehensive, real-time capable diagnostic tools that can simultaneously detect and localize multiple types of faults (e.g., heat losses, pressure drops) in District Heating Networks (DHNs), especially under transient conditions. | 1. Develop a data-driven diagnostic methodology using NARX neural networks to model DHN behavior. 2. Detect and identify both single and multiple faults (heat and pressure losses) in DHN pipes. 3. Validate the approach with a digital twin of the University of Parma DHN under both steady and transient conditions. 4. Compare three simulation architectures (Open-loop, Closed-loop, Fully Closed-loop) to determine optimal diagnostic performance. | Subsystem | DHC | Subsystem | Black-Box | Nonlinear Autoregressive Neural Network with Exogenous Inputs (NARX) | Historical data captures normal operation well. | No | - | Yes | Simulated data | N/A | N/A | Virtual testbed | A simulated digital twin of the DHN at the University of Parma campus serving 12 end-users (labs, cafeterias, etc.) | DHC | Subsystem | White-Box | Coupled hydraulic and thermal simulation | N/A | No | - | Yes | Real data | Simulink | MATLAB | - | 1min | - | - | Detection rate, Correct localization and fault type recognition | Comparisons made between open-loop, closed-loop, and fully-closed-loop architectures | No | Simulation only | Yes | Model representation limit | LEAKAGE DETECTION; STATE ESTIMATION; SYSTEM; OPTIMIZATION; PIPES; MODEL | [Losi, Enzo; Manservigi, Lucrezia; Spina, Pier Ruggero; Venturini, Mauro] Univ Ferrara, Engn Dept, Via G Saragat 1, I-44122 Ferrara, Italy | University of Ferrara | Losi, E (corresponding author), Univ Ferrara, Engn Dept, Via G Saragat 1, I-44122 Ferrara, Italy. | enzo.losi@unife.it | 2 | 2 | 38 | [5 empty] | 101355
27 | 27 | Research on the dynamic characterization and detection of refrigerant leakage in multi-connected air-conditioning system | Zhao, YF; Yang, Z; Zhu, JD; Hou, ZN; Zhang, SP; Hu, YS; Shu, Y | Zhao, Yanfeng; Yang, Zhao; Zhu, Junda; Hou, Zhaoning; Zhang, Shuping; Hu, Yansong; Shu, Yue | 2026-04-15 | 2024 | http://dx.doi.org/10.1016/j.enbuild.2024.114076 | Multi -connected air-conditioning system; Refrigerant leakage; Operational performance; Fault detection | FDD | Energy and Buildings | Existing models for refrigerant leakage detection often focus on steady-state analysis and do not account for dynamic characteristics of leakage events. Data-driven methods also rely on large historical datasets and lack real-time responsiveness. | To develop and validate a dynamic model of a Variable Refrigerant Volume (VRV) system that captures refrigerant microleakage behavior and supports real-time fault detection. A novel Python-based detection algorithm using volume change metrics is proposed and tested. | Subsystem | VRF system | Subsystem | White-Box | Physics-based component-level modeling using mass, energy, and momentum conservation laws and MBWR equation of state. | 1D flow; neglects pipe heat transfer; incompressible fluid assumption; ignores air separator and oil return temperature effects. | No | - | Yes | Lab | N/A | AMESim | Lab | Indoor and outdoor VRV units with 8 indoor evaporators, enthalpy difference chambers | - | - | - | - | - | - | - | - | - | - | - | Enthalpy chamber, Temperature sensor (Omega PT100), Pressure sensor (HRui PT3050), Data collector (YOKOGAWA GM10) | 1min | - | - | Detection time | None | Partial | Lab setup | Yes | Model representation limit | FAULT-DETECTION; BUILDING SYSTEMS; PRESSURE-DROP; HEAT-TRANSFER; 2-PHASE FLOW; DIAGNOSTICS; CHARGE; MODEL | [Zhao, Yanfeng; Yang, Zhao; Zhu, Junda; Hou, Zhaoning; Zhang, Shuping; Hu, Yansong] Tianjin Univ, State Key Lab Engines, Tianjin 300350, Peoples R China; [Shu, Yue] Hefei Gen Machinery Res Inst, State Key Lab Highend Compressor & Syst Technol, Hefei 230031, Anhui, Peoples R China | Tianjin University | Yang, Z (corresponding author), Tianjin Univ, State Key Lab Engines, Tianjin 300350, Peoples R China. | zhaoyang@tju.edu.cn | 3 | 3 | 309 | [5 empty] | 114076
28 | 28 | Energy flexibility quantification of a tropical net-zero office building using physically consistent neural network-based model predictive control | Liang, W; Li, H; Zhan, SC; Chong, AD; Hong, TZ | Liang, Wei; Li, Han; Zhan, Sicheng; Chong, Adrian; Hong, Tianzhen | JUL | 2024 | http://dx.doi.org/10.1016/j.adapen.2024.100167 | Grid-interactive efficient buildings; Energy flexibility; PV and BESS; Model predictive control (MPC); Physics-informed neural network (PINN) | EF | Advances in Applied Energy | 1. Limited exploration of energy flexibility quantification in tropical buildings, especially those using distributed energy resources (DER) like PV and BESS. 2. Lack of analysis on the impact of dynamic electricity pricing mechanisms (vs. flat-rate tariffs) in such buildings. 3. The novel Physically Consistent Neural Network (PCNN) had not yet been integrated into an MPC framework despite its control-oriented modularity. | 1. Develop a novel MPC framework based on PCNN to quantify and optimize energy flexibility. 2. Evaluate three operational scenarios in a net-zero tropical office building: flat tariff, real-time pricing (RTP), and RTP with BESS. 3. Demonstrate benefits in terms of load matching, energy efficiency, and system stability. | Subsystem | Indoor air temperature | Component | Black-Box | Physically Consistent Neural Network (PCNN), combining LSTM and RC-inspired model | Lumped air volume with ideal mixing | No | - | Yes | Real data | OSQP, CVXPY | Python | Virtual testbed | A virtualized net-zero energy office building in Singapore with rooftop PV, two DOAS units, VAV terminals, ceiling fans, and six zones | Building thermal | Component | Gray-Box | 2R2C for room, 2R1C for partition | Lumped air volume with ideal mixing | No | - | Yes | Real data | IPOPT, Optimica | Modelica | - | 5min | HVAC thermal input per zone (supply air temp*aupply airflow), BESS charging/discharging power | Medium | Demand Decrease Percentage (DDP), Energy Decrease Percentage (EDP), Self-consumption (SC), Self-sufficiency (SS) | MPC (flat-rate), MPC (RTP) | No | Simulation only | Yes | Model representation limit | SELF-CONSUMPTION; MANAGEMENT; FRAMEWORK | [Liang, Wei] Carnegie Mellon Univ, Sch Architecture, Pittsburgh, PA 15213 USA; [Liang, Wei; Li, Han; Hong, Tianzhen] Lawrence Berkeley Natl Lab, Bldg Technol & Urban Syst Div, Berkeley, CA 94720 USA; [Zhan, Sicheng; Chong, Adrian] Natl Univ Singapore, Dept Built Environm, Singapore 117566, Singapore | Carnegie Mellon University; United States Department of Energy (DOE); Lawrence Berkeley National Laboratory; National University of Singapore | Hong, TZ (corresponding author), Lawrence Berkeley Natl Lab, Bldg Technol & Urban Syst Div, Berkeley, CA 94720 USA. | thong@lbl.gov | 15 | 15 | 14 | [5 empty] | 100167
29 | 29 | Model predictive control for the ice-storage air-conditioning system coupled with multi-objective optimization | Zhao, J; Liu, DH; Yuan, XL; Wang, PP | Zhao, Jing; Liu, Dehan; Yuan, Xiulian; Wang, Peipei | 2026-04-15 | 2024 | http://dx.doi.org/10.1016/j.applthermaleng.2024.122595 | Ice-storage; Model predictive control; Multi-objective optimization; Load forecasting | CO | Applied Thermal Engineering | Existing control strategies for ice-storage air-conditioning (IAC) systems rely on fixed or heuristic rules (e.g., storage priority), which struggle to respond to dynamic building loads and time-varying electricity prices. These approaches do not support real-time optimization or precise tracking of optimal operating conditions, resulting in suboptimal energy and cost performance. | 1. Develop an intelligent control method that combines multi-objective optimization and model predictive control (MPC) for IAC systems. 2. Determine the optimal load distribution between chillers and ice storage under dynamic conditions. 3. Achieve accurate real-time tracking using MPC with a predictive model (ANN-based) and PSO optimization. | Subsystem | Chiller, TES | Component | Black-Box | Artificial Neural Network (ANN) – Backpropagation Neural Network (BPNN) with previous step states | Neglects short-term heat loss in the ice storage tank | No | - | Yes | Real data | N/A | N/A | Virtual testbed | Simulated IAC system in TRNSYS, includes chillers, ice storage tank, cooling towers, heat exchangers, and pumps | TES | Component | White-Box | TRNSYS Type module | Building side modeled as variable flow | Yes | Chiller, Cooling tower, Heat exchanger, Pump | Yes | Real data | N/A | TRNSYS | - | 1h | Chilled water supply temperature, Cooling water return temperature, Flow rate of the ice storage tank | Medium | Energy consumption, Operating cost | Ice-melting priority control strategy | No | Simulation only | Yes | Model representation limit | THERMAL-ENERGY STORAGE; COOLING SYSTEM; PERFORMANCE; TECHNOLOGIES; GUIDELINES; BUILDINGS; ALGORITHM; FORECAST; MASS | [Zhao, Jing; Liu, Dehan; Yuan, Xiulian; Wang, Peipei] Tianjin Univ, Sch Environm Sci & Engn, Tianjin Key Lab Built Environm & Energy Applicat, Tianjin 300072, Peoples R China | Tianjin University | Zhao, J (corresponding author), Tianjin Univ, Sch Environm Sci & Engn, Tianjin Key Lab Built Environm & Energy Applicat, Tianjin 300072, Peoples R China. | zhaojing@tju.edu.cn | 14 | 14 | 243 | [5 empty] | 122595
30 | 30 | Physics-Informed Neural Network Modeling and Predictive Control of District Heating Systems | de Giuli, LB; La Bella, A; Scattolini, R | de Giuli, Laura Boca; La Bella, Alessio; Scattolini, Riccardo | JUL | 2024 | http://dx.doi.org/10.1109/TCST.2024.3355476 | District heating systems (DHSs); nonlinear model predictive control (NMPC); physics-informed recurrent neural networks (PI-RNNs) | CO | IEEE Transactions on Control Systems Technology | Traditional physical models of district heating systems (DHSs) are computationally intensive due to their complexity and high-dimensional parameter space. Data-driven models like RNNs lack physical consistency and require large datasets. There was a need for a model that combines physical insight with data-driven efficiency to enable scalable predictive control strategies. | 1. Propose a physics-informed recurrent neural network (PI-RNN) modeling method that leverages known DHS topology. 2. Use the PI-RNN for nonlinear model predictive control (NMPC) to improve efficiency and reduce production costs with tractable computation. | Subsystem | DHC | Subsystem | Black-Box | Physics-Informed Recurrent Neural Networks (PI-RNN), physics-informed via topology. | Neglects internal dynamics of heat exchangers. | No | - | Yes | Simulated data | SSNET Library | Python | Virtual testbed | AROMA DHS simulator in Modelica; 9-node DHS network with 5 thermal loads and 7262.4 m of pipelines. | DHC | Subsystem | White-Box | Modelica-based models | N/A | No | - | Yes | Validated platform | DHN4Control Library | Modelica | - | 5min | Heating station supply temperature | Medium | Production cost, Total thermal losses, Average computational time | Rule-based strategy (constant supply temperature) | No | Simulation only | Yes | Model representation limit | STRATEGIES; OPTIMIZATION; COEFFICIENT; PERFORMANCE | [de Giuli, Laura Boca; La Bella, Alessio; Scattolini, Riccardo] Politecn Milan, Dipartimento Elettron Informaz & Bioingn, I-20133 Milan, Italy | Polytechnic University of Milan | La Bella, A (corresponding author), Politecn Milan, Dipartimento Elettron Informaz & Bioingn, I-20133 Milan, Italy. | laura.bocadegiuli@polimi.it; alessio.labella@polimi.it; riccardo.scattolini@polimi.it | 12 | 12 | 32 | 4 |  |  | 1182 | 1195
31 | 31 | Development and performance evaluation of intelligent algorithm for optimal control of a hybrid heat pump system during the cooling season | Jung, YG; Lee, KH; Park, BR; Kim, RATW; Moon, JW | Jung, Yong Gi; Lee, Kwang Ho; Park, Bo Rang; Kim, rk a Tae Won; Moon, Jin Woo | 2026-03-01 | 2024 | http://dx.doi.org/10.1016/j.enbuild.2024.113934 | Hybrid Heat Pump System; Artificial Neural Network; Intelligent Optimal Control; Heat Storage Tank; Indoor | CO | Energy and Buildings | Existing hybrid heat pump systems typically use rule-based or PID control, which struggle with system integration, adaptability to real-time load variations, and nonlinear characteristics of system components. Prior works have mostly focused on predictive modeling for single heat sources and lacked actual control studies and integrated control strategies. | To develop and validate an ANN-based optimal control algorithm that improves the cooling-period performance of a hybrid heat pump system, enhancing control accuracy and energy efficiency through predictive modeling of heat storage tank (HST) and indoor temperatures. | Subsystem | Indoor air temperature, TES | Component | Black-Box | Deep Neural Network (DNN) with 3 and 4 hidden layers respectively, training on simulation data from TRNSYS models | Input variables assumed to be adequate for temperature dynamics | No | - | Yes | Real data | N/A | N/A | Real building | Located in Busan, Korea (Cfa climate zone), 110.16 m² floor area. Hybrid heat pump system includes PVT and air-source heat pumps with a 300 L HST and Fan Coil Units. Real-time data acquisition and control through WEP-based cloud and MQTT protocol. | - | - | - | - | - | - | - | - | - | - | - | WEP-based cloud platform linked to Internet of Things devices with sensing data stored in an SQL database; MQTT protocol | 10min | Circulation pump flow rate | Medium | HST temperature, Indoor temperature, Energy consumption | Rule-based control strategy (on/off deadband logic) | Yes | Full-scale real-world deployment | Yes | Model representation limit | ENERGY; PREDICTION | [Jung, Yong Gi; Moon, Jin Woo] Chung Ang Univ, Sch Architecture & Bldg Sci, 84 Heukseok Ro, Seoul 06974, South Korea; [Lee, Kwang Ho] Korea Univ, Coll Engn, Dept Architecture, 145 Anam Ro, Seoul 02841, South Korea | Chung Ang University; Korea University | Moon, JW (corresponding author), Chung Ang Univ, Sch Architecture & Bldg Sci, 84 Heukseok Ro, Seoul 06974, South Korea. | xngilsh@cau.ac.kr; kwhlee@korea.ac.kr; pbrighten@cau.ac.kr; xngilsh@cau.ac.kr; gilerbert73@cau.ac.kr | 10 | 10 | 306 | [5 empty] | 113934
32 | 32 | Model Predictive Control of Variable Refrigerant Flow Systems for Room Temperature Control | Lin, CY; Liao, TK; Chou, HH; Wu, YC; Wang, CC; Nian, SH; Tsai, MY; Hung, TW | Lin, Chun-Yeon; Liao, Ting-Kuan; Chou, Hsin-Hao; Wu, Yi-Chin; Wang, Chien-Chang; Nian, Shy-Her; Tsai, Meng-Yen; Hung, Tsai-Wang |  | 2024 | http://dx.doi.org/10.1109/ACCESS.2024.3439890 | Temperature control; Switches; Control systems; Predictive control; Refrigeration; Predictive models; Numerical models; Refrigerants; Variable refrigerant flow system; model predictive control; room temperature | CO | IEEE Access | 1. Most physical models for one-to-many VRF systems are complex and hard to parametrize. 2. Temperature control is difficult due to interference among indoor units (superheat/room temperature coupling). 3. Existing system identification models offer limited accurate control over narrow temperature ranges. | 1. Develop a supervisor model-switch strategy with system identification for VRF systems. 2. Use MPC to control room and superheat temperatures robustly. 3. Enable smooth switching among multiple linear models for wider temperature control range. 4. Experimentally validate performance on a one-to-three VRF system. | Subsystem | VRF system | Subsystem | Gray-Box | First-order linear transfer functions identified via system identification with energy conservation-based approximations | Two-phase region of evaporator dominates heat exchange, Room dynamics approximated by lumped thermal capacity | No | - | Yes | Lab | N/A | N/A | Lab | One-to-three VRF setup, Three indoor units with heaters and fixed thermal loads, Simulated outdoor room at 35°C (Room 5 with 14 kW condenser), Experimental refrigerant: R-410A | - | - | - | - | - | - | - | - | - | - | - | N/A | 40s | Compressor speed, EEV openings | Low | Indoor temperature steady-state error, Energy consumption | None | Partial | Lab setup | Yes | Model representation limit | NONLINEAR-SYSTEMS; TIME; IDENTIFICATION; STABILITY; MPC | [Lin, Chun-Yeon; Liao, Ting-Kuan; Chou, Hsin-Hao; Wu, Yi-Chin] Natl Taiwan Univ, Dept Mech Engn, Taipei 10617, Taiwan; [Wang, Chien-Chang; Nian, Shy-Her; Tsai, Meng-Yen; Hung, Tsai-Wang] Ind Technol Res Inst, Green Energy & Environm Res Labs, Hsinchu 31040, Taiwan | National Taiwan University; Industrial Technology Research Institute - Taiwan | Lin, CY (corresponding author), Natl Taiwan Univ, Dept Mech Engn, Taipei 10617, Taiwan. | chunyeonlin@ntu.edu.tw | 0 | 0 | 12 |  |  |  | 123193 | 123207
33 | 33 | Adaptive Model Predictive Controller for Building Thermal Dynamics | Tohidi, SS; Calì, D; Madsen, H | Tohidi, Seyed Shahabaldin; Cali, Davide; Madsen, Henrik |  | 2024 | http://dx.doi.org/10.1109/LCSYS.2024.3410170 | Model predictive control; building thermal dynamics; adaptive parameter identification; energy systems; stability analysis | CO | IEEE Control Systems Letters | Conventional MPC for buildings depends on accurate system models, which are costly and data-intensive to develop. Moreover, these models are often time-invariant and fail to adapt to system changes (e.g., faults, aging, weather variations), leading to degraded performance over time. | 1. Develop an adaptive MPC that eliminates the need for a highly accurate, fixed model by updating model parameters online. 2. Introduce an adaptive parameter identification algorithm with convergence guarantees. 3. Design a boundedness-preserving MPC with an additional constraint to maintain system stability despite parameter changes. 4. Demonstrate that the controller performs well using simulation, even when thermal parameters change mid-simulation (e.g., improved insulation). | Subsystem | Building thermal | Component | Gray-Box | Linear RC (resistor-capacitor) thermal circuit model. | Assumes linear dynamics with an additional nonlinear residual term. | No | - | Yes | Simulated data | N/A | N/A | Virtual testbed | Two-state thermal zone model using parameters from literature. Simulates a building zone with an envelope and interior zone where insulation changes at t = 30 hours. | Building thermal | Component | White-Box | Linear RC (resistor-capacitor) thermal circuit model with known RC parameters | Assumes linear dynamics with an additional nonlinear residual term. | No | - | Yes | Previous Literature | N/A | N/A | - | N/A | Heating/cooling input power | Medium | Indoor temperature, Energy consumption, Stability | Compared against conventional MPC that does not adapt to changes in thermal dynamics. | No | Simulation only | Yes | The process model and testbed are the same | DEMAND RESPONSE; ENERGY; SYSTEMS; MANAGEMENT; COMPLEXITY | [Tohidi, Seyed Shahabaldin; Cali, Davide; Madsen, Henrik] Tech Univ Denmark, Dept Appl Math & Comp Sci, DK-2800 Lyngby, Denmark | Technical University of Denmark | Tohidi, SS (corresponding author), Tech Univ Denmark, Dept Appl Math & Comp Sci, DK-2800 Lyngby, Denmark. | sshto@dtu.dk; dcal@dtu.dk; hmad@dtu.dk | 1 | 1 | 8 |  |  |  | 1325 | 1330
34 | 34 | District Cooling System Control for Providing Operating Reserve Based on Safe Deep Reinforcement Learning | Yu, PP; Zhang, HC; Song, YH; Hui, HX; Chen, G | Yu, Peipei; Zhang, Hongcai; Song, Yonghua; Hui, Hongxun; Chen, Ge | JAN | 2024 | http://dx.doi.org/10.1109/TPWRS.2023.3237888 | Cooling; Buildings; HVAC; Uncertainty; Power demand; Power system dynamics; Real-time systems; District cooling system; operating reserve; model-free control; safe deep reinforcement learning | EF | IEEE Transactions on Power Systems | Existing works have focused on day-ahead or hour-ahead scheduling of district cooling systems (DCS) or residential HVACs, often relying on conventional control methods (e.g., MPC, MILP, heuristics) that struggle with real-time uncertainty and high system complexity. No prior work addresses real-time DCS control for providing operating reserve using safe deep reinforcement learning (safe-DRL). | 1. Formulate DCS control as an MDP for real-time operating reserve while maintaining indoor comfort. 2. Develop a safe-DRL controller (safe-DDPG) with a safety layer to satisfy critical constraints (e.g., power caps). 3. Introduce a self-adaptive target function to suppress power rebound during recovery. | Whole System | Building thermal | Component | White-Box | Energy balance | Lumped air volume with ideal mixing | Yes | Chillers, Heat exchangers | No | None | N/A | N/A | Virtual testbed | Simulated DCS same to environment | Building thermal | Component | White-Box | Energy balance | Lumped air volume with ideal mixing | Yes | Chillers, Heat exchangers | No | None | N/A | N/A | - | 15min | Water valves (mass flow rate of chilled water to each building) | Low | Deviation from set temperature, Power cap compliance, Peak power rebound, Convergence reward, Sample efficiency, Number of uncomfortable buildings | PI controller, Model Predictive Control (MPC), Conventional DDPG (DRL without safe layer) | No | Simulation only | No | The process model (environment) and testbed are the same | SYNCHRONOUS CONDENSERS; TRANSIENT STABILITY; ALLOCATION; CONVERTERS; WIND | [Yu, Peipei; Zhang, Hongcai; Song, Yonghua; Hui, Hongxun; Chen, Ge] Univ Macau, State Key Lab Internet Things Smart City, Macau 999078, Peoples R China; [Yu, Peipei; Zhang, Hongcai; Song, Yonghua; Hui, Hongxun; Chen, Ge] Univ Macau, Dept Elect & Comp Engn, Macau 999078, Peoples R China | University of Macau; University of Macau | Zhang, HC (corresponding author), Univ Macau, State Key Lab Internet Things Smart City, Macau 999078, Peoples R China.;Zhang, HC (corresponding author), Univ Macau, Dept Elect & Comp Engn, Macau 999078, Peoples R China. | yc07431@connect.um.edu.mo; hczhang@um.edu.mo; yhsong@um.edu.mo; hongxunhui@um.edu.mo; yb97431@connect.um.edu.mo | 18 | 18 | 39 | 1 |  |  | 40 | 52
35 | 35 | Intelligent control of district heating system based on RDPG | Gong, MJ; Liu, Y; Sun, JW; Xu, W; Li, WX; Yan, CC; Fu, WC | Gong, Mingju; Liu, Yan; Sun, Jiawang; Xu, Wei; Li, Wenxiang; Yan, Changcheng; Fu, Wencheng | MAR | 2024 | http://dx.doi.org/10.1016/j.engappai.2023.107672 | District heating system; Recurrent deterministic policy gradient; Long short-term memory; Heat supply secondary pipe network | CO | Engineering Applications of Artificial Intelligence | Most prior studies focused on the primary circuit of district heating systems (DHS) and did not adequately model the thermal inertia and nonlinear time-delay characteristics of the secondary network and indoor environment. There was also a lack of intelligent control mechanisms that utilize temporal data dependencies. | 1. Propose a deep reinforcement learning (DRL) strategy using the Recurrent Deterministic Policy Gradient (RDPG) algorithm enhanced with Long Short-Term Memory (LSTM) for DHS control. 2. Model critical components of the secondary DHS (plate heat exchanger, secondary heating network, heat users) considering thermal inertia. | Subsystem | Building thermal, District pipe network, HX | Subsystem | White-Box | Energy balance equations (mass and energy conservation) | Heat exchanger loss is negligible, Fixed soil temperature | No | - | Yes | Real data | N/A | Python | Virtual testbed | Same as application model: Simulated district heating system including plate heat exchanger, secondary pipe network, and indoor heating system | Building thermal, District pipe network, HX | Subsystem | White-Box | Energy balance equations (mass and energy conservation) | Heat exchanger loss is negligible, Fixed soil temperature | No | - | Yes | Real data | N/A | Python | - | 1h | Supply water temperature | Medium | Indoor temperature, Heat load, Convergence speed, Training stability | PID controller, DRL baselines: DDPG, TD3, DPPO, A3C | No | Simulation only | No | The process model (environment) and testbed are the same | ENERGY-CONSUMPTION; THERMAL INERTIA; CHINA; MODEL; BUILDINGS; OPERATION; SECTOR | [Gong, Mingju; Liu, Yan; Sun, Jiawang; Li, Wenxiang; Yan, Changcheng] Tianjin Univ Technol, Sch Integrated Circuit Sci & Engn, Tianjin Key Lab Thin Film Elect & Commun Devices, Tianjin 300384, Peoples R China; [Xu, Wei] Tianjin Univ Technol, Inst Marine Intelligent Construction, Tianjin 300384, Peoples R China; [Xu, Wei] Sea Area & Isl Environm Sci & Technol Res Inst Tia, Tianjin, Peoples R China; [Fu, Wencheng] Tianjin Univ Technol, Sch Mech Engn, Tianjin 300384, Peoples R China | Tianjin University of Technology; Tianjin University of Technology; Tianjin University of Technology | Sun, JW (corresponding author), Tianjin Univ Technol, Sch Integrated Circuit Sci & Engn, Tianjin Key Lab Thin Film Elect & Commun Devices, Tianjin 300384, Peoples R China. | itjwsun@163.com | 4 | 4 | 129 | [5 empty] | 107672
36 | 36 | Optimization of Air Handler Controllers for Comfort Level in Smart Buildings Using Nature Inspired Algorithm | Aziz, M; Kadir, K; Azman, HK; Vijyakumar, K | Aziz, Miqdad; Kadir, Kushsairy; Azman, Haziq Kamarul; Vijyakumar, Kanendra | DEC | 2023 | http://dx.doi.org/10.3390/en16248064 | air-conditioning and mechanical ventilation; air handling unit; energy efficiency; firefly algorithm; particle swarm optimization; smart building; thermal comfort | CO | Energies | The study identifies a lack of effective control strategies for temperature regulation in building sub-levels, particularly in the context of HVAC systems operating in tropical climates. Traditional PID controllers are inadequate for ensuring occupant comfort and energy efficiency. | To improve the control of AHU (Air Handling Unit) temperature using nature-inspired optimization algorithms—specifically Firefly Algorithm (FA) and Particle Swarm Optimization (PSO)—in combination with PID controllers. | Subsystem | Building thermal | Component | Black-Box | Nonlinear AutoRegressive with eXogenous input (NL-ARX) | Lumped air volume with ideal mixing | No | - | Yes | Real data | N/A | N/A | Virtual testbed | Same as application model | Building thermal | Component | Black-Box | Nonlinear AutoRegressive with eXogenous input (NL-ARX) | Lumped air volume with ideal mixing | No | - | Yes | Real data | N/A | N/A | - | N/A | Supply air temperature, Fan speed, Chilled water flow rate | Low, Medium | PMV | Conventional PID | No | Simulation only | No | The process model and testbed are the same | THERMAL COMFORT; SIMULATION-OPTIMIZATION; ENERGY EFFICIENCY; SYSTEMS; TEMPERATURE; PREDICTION; MANAGEMENT; MALAYSIA; MODELS | [Aziz, Miqdad; Kadir, Kushsairy] Univ Kuala Lumpur, British Malaysian Inst UniKL BMI, Dept Elect Technol Sect, Kuala Lumpur 53100, Malaysia; [Azman, Haziq Kamarul] Univ Kuala Lumpur, British Malaysian Inst UniKL BMI, Dept Elect Engn Sect, Kuala Lumpur 53100, Malaysia; [Vijyakumar, Kanendra] Univ Teknol MARA UiTM, Dept Elect Engn, Shah Alam 40450, Malaysia | University of Kuala Lumpur; University of Kuala Lumpur; Universiti Teknologi MARA | Aziz, M (corresponding author), Univ Kuala Lumpur, British Malaysian Inst UniKL BMI, Dept Elect Technol Sect, Kuala Lumpur 53100, Malaysia. | mmiqdad@unikl.edu.my | 2 | 2 | 16 | 24 |  |  |  |  | 8064
37 | 37 | A new model predictive control approach integrating physical and data-driven modelling for improved energy performance of district heating substations | Zhang, ZH; Zhou, XL; Du, H; Cui, P | Zhang, Zhihao; Zhou, Xinlei; Du, Han; Cui, Ping | 2026-12-15 | 2023 | http://dx.doi.org/10.1016/j.enbuild.2023.113688 | Model predictive control; District heating system; Machine learning; Physical modelling | CO | Energy and Buildings | Existing district heating (DH) control strategies typically rely on fuzzy logic or rule-based systems that do not account for indoor feedback or system inertia, resulting in inefficiencies and suboptimal comfort. Moreover, pure data-driven MPC models risk overfitting and lack interpretability, while physical models are labor-intensive to calibrate. | The study aims to develop a hybrid MPC approach that integrates a reduced-order physical model with a data-driven predictive model (LSTM + BPNN) to optimize DH substation operations for better energy efficiency and thermal comfort. | Subsystem | Indoor air temperature | Component | Black-Box | LSTM for indoor temperature prediction | Lumped air volume with ideal mixing | No | - | Yes | Real data | N/A | N/A | Virtual testbed | Same as application model | Indoor air temperature | Component | Black-Box | LSTM for indoor temperature prediction, BPNN for return temperature prediction | Lumped air volume with ideal mixing | No | - | Yes | Real data | N/A | N/A | - | 1h | Supply water temperature | Medium | Indoor temperature, Energy consumption | Fuzzy rule-based control, Physical model only, Pure data-driven MPC | No | Simulation only | No | The process model and testbed are the same | OPTIMIZATION | [Zhang, Zhihao; Cui, Ping] Shandong Jianzhu Univ, Sch Thermal Energy Engn, Jinan 250101, Peoples R China; [Zhou, Xinlei; Du, Han] Univ Wollongong, Sustainable Bldg Res Ctr, Wollongong 2522, Australia | Shandong Jianzhu University; University of Wollongong | Cui, P (corresponding author), Shandong Jianzhu Univ, Sch Thermal Energy Engn, Jinan 250101, Peoples R China.;Zhou, XL (corresponding author), Univ Wollongong, Sustainable Bldg Res Ctr, Wollongong 2522, Australia. | xz966@uowmail.edu.au; sdcuiping@sdjzu.edu.cn | 4 | 4 | 301 | [5 empty] | 113688
38 | 38 | Difference analysis and recognition of hydraulic oscillation by two types of sudden faults on long-distance district heating pipeline | Yan, JJ; Zhang, H; Wang, YR; Zhu, ZZ; Bai, H; Li, QC; Zheng, LJ; Gao, XY; You, SJ | Yan, Jingjing; Zhang, Huan; Wang, Yaran; Zhu, Zhaozhe; Bai, He; Li, Qicheng; Zheng, Lijun; Gao, Xinyong; You, Shijun | 2026-12-01 | 2023 | http://dx.doi.org/10.1016/j.energy.2023.128696 | Difference analysis; Hydraulic oscillation; Sudden faults recognition; Long-distance district heating pipeline | FDD | Energy | There is limited work on real-time fault detection in long-distance district heating pipelines (LDHP), particularly in recognizing and distinguishing between different types of sudden faults (leakage vs. valve failure) using dynamic hydraulic behavior. Existing methods often assume prior knowledge of fault type or are limited to steady-state modeling. | 1. Analyze the difference in hydraulic oscillation patterns induced by leakage and valve failure. 2. Propose a novel fault recognition method that combines a hydraulic transient model with Support Vector Machine (SVM) and Particle Swarm Optimization (PSO). 3. Accurately identify the type, location, and status of the fault under dynamic conditions. | Subsystem | District pipe network | Component | White-Box | Finite difference-based numerical solution of hydraulic transient equations derived from mass and momentum conservation | Single fault (either leakage or valve failure) occurs at a time | No | - | No | None | N/A | Python | Virtual testbed | Same as application model: A numerically simulated 20 km LDHP with 900 mm diameter, constant pressure source, and simplified hydraulic boundary conditions | District pipe network | Component | White-Box | Finite difference-based numerical solution of hydraulic transient equations derived from mass and momentum conservation | Single fault (either leakage or valve failure) occurs at a time | No | - | No | None | N/A | Python | - | 0.5s | - | - | Fault classification accuracy, Absolute and relative location errors, Status estimation error, Robustness under sensor noise and varying sampling periods | None | No | Simulation only | No | The process model and testbed are the same | SYSTEM; OPTIMIZATION; MODEL | [Yan, Jingjing; Zhang, Huan; Wang, Yaran; You, Shijun] Tianjin Univ, Sch Environm Sci & Engn, Tianjin 300072, Peoples R China; [Zhu, Zhaozhe; Bai, He; Li, Qicheng] Tianjin Chengan Thermal Power Co Ltd, Tianjin 300204, Peoples R China; [Zhang, Huan; Wang, Yaran; You, Shijun] Tianjin Key Lab Biomass Wastes Utilizat, Tianjin 300350, Peoples R China; [Zheng, Lijun; Gao, Xinyong] Huadian Elect Power Res Inst Co Ltd, Hangzhou 310030, Peoples R China | Tianjin University | Wang, YR (corresponding author), Tianjin Univ, Sch Environm Sci & Engn, Tianjin 300072, Peoples R China. | yaran_wang@tju.edu.cn | 6 | 6 | 284 | [5 empty] | 128696
39 | 39 | Graph neural network-based spatio-temporal indoor environment prediction and optimal control for central air-conditioning systems | Zhang, J; Xiao, F; Li, A; Ma, TY; Xu, K; Zhang, HB; Yan, R; Fang, X; Li, YY; Wang, D | Zhang, Jing; Xiao, Fu; Li, Ao; Ma, Tianyou; Xu, Kan; Zhang, Hanbei; Yan, Rui; Fang, Xing; Li, Yuanyang; Wang, Dan | 2026-08-15 | 2023 | http://dx.doi.org/10.1016/j.buildenv.2023.110600 | Machine learning; Graph neural network; Indoor environment; Optimal control; Air conditioning system | CO | Building and Environment | Traditional control strategies for HVAC systems assume a well-mixed, spatially uniform temperature distribution, often relying on single-point or averaged sensor measurements. This fails to reflect the actual spatial variability of indoor air temperature, particularly in large, complex spaces. Existing data-driven models mostly capture temporal correlations, neglecting spatial ones. | 1. Develop a spatio-temporal GNN-RNN model for predicting the distributed indoor environment (temperature, CO₂) by integrating multi-source data (BIM, BAS, IoT). 2. Propose a model-based online optimal control strategy that uses the learned spatio-temporal dynamics to optimize indoor thermal comfort via VAV setpoints in a real AHU-VAV system. | Subsystem | Indoor temperature field | Component | Black-Box | GNN-RNN architecture (specifically GAT-RNN, GCN-RNN, DC-RNN variants). | N/A | No | - | Yes | Real data | Keras, Spektral, Scikit-optimize | Python | Real building | AHU-VAV system in a real high-rise office building (Foshan, China); includes private offices and open-plan areas; 12 VAV boxes, 22 IoT sensors, 1 AHU; | - | - | - | - | - | - | - | - | - | - | - | Cloud platform, BAS, IoT sensors, Influxdb temporal database | 10min | Temperature difference between the return air temperature and the indoor air temperature setpoint of all VAV boxes | Medium | Indoor temperature | Existing rule-based control strategy with fixed setpoints | Yes | Full-scale real-world deployment | Yes | Model representation limit | THERMAL COMFORT; OPTIMIZATION; MODELS | [Zhang, Jing; Xiao, Fu; Li, Ao; Ma, Tianyou; Xu, Kan; Zhang, Hanbei] Hong Kong Polytech Univ, Dept Bldg Environm & Energy Engn, Hong Kong, Peoples R China; [Xiao, Fu] Hong Kong Polytech Univ, Res Inst Smart Energy, Hong Kong, Peoples R China; [Yan, Rui; Fang, Xing; Li, Yuanyang] Midea Grp, Midea Bldg Technol Div, Foshan 528311, Guangdong, Peoples R China; [Wang, Dan] Hong Kong Polytech Univ, Dept Comp, Hong Kong, Peoples R China | Hong Kong Polytechnic University; Hong Kong Polytechnic University; Midea; Hong Kong Polytechnic University | Xiao, F (corresponding author), Hong Kong Polytech Univ, Dept Bldg Environm & Energy Engn, Hong Kong, Peoples R China. | linda.xiao@polyu.edu.hk | 32 | 33 | 242 | [5 empty] | 110600
40 | 40 | Energy-efficient control of indoor PM2.5 and thermal comfort in a real room using deep reinforcement learning | An, YT; Chen, C | An, Yuting; Chen, Chun | 2026-09-15 | 2023 | http://dx.doi.org/10.1016/j.enbuild.2023.113340 | Smart home; Deep reinforcement learning; IndoorPM2; 5; Thermal comfort; Energy consumption | CO | Energy and Buildings | Most previous studies using DRL for indoor air quality and thermal comfort control are evaluated in simulations. There's a lack of experimental validation in real environments, especially for systems controlling multiple devices (window, air cleaner, air conditioner) under varying indoor PM2.5 and thermal comfort conditions. | Develop a DQN-based smart controller for simultaneous control of window, air cleaner, and air conditioner to reduce indoor PM2.5, maintain thermal comfort, and minimize energy consumption. Validate its performance in a real room and compare with a baseline controller. | Component | Building thermal, IAQ | Component | Gray-Box | PM2.5: Particle dynamics ODE (mass balance model with source, sink, and ventilation terms); Thermal: Energy balance equation (ODE considering heat transfer and internal/external gains); Key parameters are estimated from real data using regression/grid search | Simplified indoor heat gain and AC output | No | - | Yes | Real data | N/A | N/A | Real building | Real room in Hong Kong (14 m², 3 m high); tested for 4 days; equipped with window actuator, air cleaner (CADR = 400 m³/h), portable AC (cooling = 2200 W); real-time sensors and cloud-based controller. | - | - | - | - | - | - | - | - | - | - | - | RS485 interface, Modbus protocol, Wi-Fi, Smart plug, Arizona test dust with particle generator | 5 min (AC/window), 1 min (air cleaner) | Window (open/close), Air cleaner (on/off), Air conditioner (on/off) | Low | Indoor PM2.5, Indoor temperature | Rule-based baseline controller from occupant survey (n=249, the option chosen by the most people was selected as the rule of the baseline.) | Yes | Full-scale real-world deployment | Yes | Model representation limit | EMISSION RATES; AIR-POLLUTION; PARTICLES; PERFORMANCE; PENETRATION; BUILDINGS; BEHAVIOR; EXPOSURE; SYSTEMS; MODEL | [An, Yuting; Chen, Chun] Chinese Univ Hong Kong, Dept Mech & Automat Engn, Shatin, Hong Kong 999077, Peoples R China; [Chen, Chun] Chinese Univ Hong Kong, Inst Environm Energy & Sustainabil, Shatin, Hong Kong 999077, Peoples R China | Chinese University of Hong Kong; Chinese University of Hong Kong | Chen, C (corresponding author), Chinese Univ Hong Kong, Dept Mech & Automat Engn, Shatin, Hong Kong 999077, Peoples R China. | chunchen@mae.cuhk.edu.hk | 18 | 18 | 295 | [5 empty] | 113340
41 | 41 | Dynamic modeling and flexible control of combined heat and power units integrated with thermal energy storage system | Wang, XY; Dong, LJ; Zhu, Q; Li, YJ; Han, HZ; Liang, JH; Duan, BD | Wang, Xiaoyu; Dong, Lijiang; Zhu, Qing; Li, Yongji; Han, Hongzhi; Liang, Jiahao; Duan, Bingde | NOV | 2023 | http://dx.doi.org/10.1016/j.egyr.2023.06.027 | Combined heat and power; Thermal energy storage system; Coordinated control system control; Operating flexibility; Linear quadratic regulator | CO | Energy Reports | Most existing studies on CHP systems with Thermal Energy Storage (TES) focus on static dispatch strategies and overlook the dynamic control process required for real-time flexibility under high renewable energy penetration. Additionally, coordinated control strategies for CHP systems that can decouple power and heat while preserving system responsiveness are lacking. | 1. Develop a dynamic model of a 300 MW Combined Heat and Power (CHP) unit integrated with a TES system. 2. Propose and test a coordinated control strategy based on a Linear Quadratic Regulator (LQR) for improved power ramp rate and thermal stability. | Subsystem | CHP, TES | Subsystem | White-Box | First-principles, physics-based dynamic modeling using mass and energy balances. State-space model formulation is derived from differential equations describing coal combustion, steam generation, turbine power output, and TES heat exchange. | Linearization for LQR design | No | - | No | None | N/A | MATLAB | Virtual testbed | Simulation-based test of a 300 MW CHP system with integrated TES | CHP, TES | Subsystem | White-Box | First-principles, physics-based dynamic modeling using mass and energy balances. State-space model formulation is derived from differential equations describing coal combustion, steam generation, turbine power output, and TES heat exchange. | Linearization for LQR design | No | - | No | None | Simulink | MATLAB | - | 1s | Feed-coal mass flow rate, Turbine valve position, Heat source valve position, TES inlet/outlet valve positions | Low | Electrical power output, Main steam pressure output, Intermediate-pressure cylinder outlet pressure output, Equivalent heat source steam flow output, Water level and thermocline stability in TES | Conventional Coordinated Control Strategy (CCS) using PID controllers for boiler-following-turbine scheme. | No | Simulation only | No | The process model and testbed are the same | SOLAR | [Wang, Xiaoyu; Dong, Lijiang; Duan, Bingde] Xinjiang Xinneng Grp, Urumqi Elect Power Construct & Commissioning Inst, Urumqi 830011, Peoples R China; [Wang, Xiaoyu; Li, Yongji; Han, Hongzhi; Liang, Jiahao] State Grid Xinjiang Co Ltd, Elect Power Res Inst, Urumqi 830011, Peoples R China; [Zhu, Qing] State Grid Xinjiang Elect Power Co Ltd, Urumqi 830002, Peoples R China | State Grid Corporation of China | Han, HZ (corresponding author), State Grid Xinjiang Co Ltd, Elect Power Res Inst, Urumqi 830011, Peoples R China. | hhz20222022@163.com | 7 | 7 | 10 |  |  |  | 396 | 406
42 | 42 | Adaptive model predictive control with ensembled multi-time scale deep-learning models for smart control of natural ventilation | Chen, EX; Han, X; Malkawi, A; Zhang, RY; Li, N | Chen, Elence Xinzhu; Han, Xu; Malkawi, Ali; Zhang, Runyu; Li, Na | 2026-08-15 | 2023 | http://dx.doi.org/10.1016/j.buildenv.2023.110519 | Model predictive control; Adaptive control; Machine learning; Multi-objective control optimization; Building system control; Natural ventilation | CO | Building and Environment | Traditional MPC for natural ventilation struggles with nonlinear system dynamics, accurate long-horizon predictions, and time-varying uncertainties. Existing models often demand high manual modeling effort and are brittle in adapting to environmental changes. | 1. Develop an Ensembled Multi-time scale Adaptive MPC (EMA-MPC) system. 2. Integrate short- and long-term deep learning models for improved dynamic modeling. 3. Use online model adaptation and bound control for robustness. 4. Demonstrate improved control of natural ventilation via a case study. | Component | Building thermal, IAQ | Component | Black-Box | Ensembled-LSTM (two LSTMs for fast/slow timescales) | Lumped air volume with ideal mixing | No | - | Yes | Simulated data | Keras, Scikit-optimize | Python | Virtual testbed | A Modelica-based testbed simulates a single-sided naturally ventilated room with radiant floor heating. The room is part of HouseZero at Harvard, with validated physics-based thermal models using real operational data (RMSE ~0.73 K). | Building thermal, IAQ | Component | White-Box | Modelica Buildings Library-based modelling | High-fidelity model, no major simplifying assumptions beyond library defaults. | Yes | Natural ventilation | Yes | Real data | Modelica Buildings Library | Modelica | - | 15min | Window opening angle and duration | Low | Indoor CO₂ concentration, Indoor air temperature, Heating demand | Rule-Based Control (RBC), Basic MPC (non-adaptive model), Enhanced MPC (non-adaptive with bound control) | No | Simulation only | Yes | Model representation limit | BUILDINGS; SYSTEMS; HVAC; OPTIMIZATION; MPC | [Chen, Elence Xinzhu; Han, Xu; Malkawi, Ali] Harvard Univ, Grad Sch Design, Cambridge, MA 02138 USA; [Chen, Elence Xinzhu; Han, Xu; Malkawi, Ali] Harvard Univ, Harvard Ctr Green Bldg & Cities, Cambridge, MA 02138 USA; [Zhang, Runyu; Li, Na] Harvard Univ, John A Paulson Sch Engn & Appl Sci, Cambridge, MA 02138 USA; [Han, Xu] 20 Sumner Rd, Cambridge, MA 02138 USA | Harvard University; Harvard University; Harvard University | Han, X (corresponding author), 20 Sumner Rd, Cambridge, MA 02138 USA. | xu.han@gsd.harvard.edu | 14 | 14 | 242 | [5 empty] | 110519
43 | 43 | District cooling system control for providing regulation services based on safe reinforcement learning with barrier functions | Yu, PP; Zhang, HC; Song, YH | Yu, Peipei; Zhang, Hongcai; Song, Yonghua | 2026-10-01 | 2023 | http://dx.doi.org/10.1016/j.apenergy.2023.121396 | Safe deep reinforcement learning; District cooling system; Frequency regulation service; Control barrier function | EF | Applied Energy | Prior research focused mainly on using district cooling systems (DCSs) for minimizing energy costs or improving efficiency, but not on their potential to provide regulation services to the grid. Challenges include complex thermal dynamics and uncertainties from regulation signals and cooling demands. | 1. Develop a safe deep reinforcement learning (DRL) method using a control barrier function (CBF) to ensure safety during training. 2. Propose a two-stage DCS control framework for real-time power regulation. 3. Enhance training efficiency while guaranteeing system safety. | Subsystem | Building thermal | Component | White-Box | Energy balance | Lumped air volume with ideal mixing | Yes | Chiller | No | None | N/A | Python | Virtual testbed | Same as application model: A simulated DCS serving 12 buildings | Building thermal | Component | White-Box | Energy balance | Lumped air volume with ideal mixing | Yes | Chiller | No | None | N/A | Python | - | 2s | Stage 1: Total chilled water mass flow; Stage 2: Water mass flow distribution across buildings | Medium | Regulation signal tracking error, Temperature deviation across buildings, Regulation performance score, Sample efficiency and convergence reward | PI control, DDPG without safety layer | No | Simulation only | No | The process model (environment) and testbed are the same | OPTIMIZATION; INTEGRATION; STORAGE | [Zhang, Hongcai] Univ Macau, State Key Lab Internet Things Smart City, Macau, Peoples R China; Univ Macau, Dept Elect & Comp Engn, Macau, Peoples R China | University of Macau; University of Macau | Zhang, HC (corresponding author), Univ Macau, State Key Lab Internet Things Smart City, Macau, Peoples R China. | hczhang@um.edu.mo | 10 | 11 | 347 | [5 empty] | 121396
44 | 44 | Model predictive control of short-term winter natural ventilation in a smart building using machine learning algorithms | Zhang, W; Wu, WT; Norford, L; Li, N; Malkawi, A | Zhang, Wei; Wu, Wentao; Norford, Leslie; Li, Na; Malkawi, Ali | 2026-08-15 | 2023 | http://dx.doi.org/10.1016/j.jobe.2023.106602 | Machine learning; Single sided ventilation; Operable window; MPC; Natural ventilation; Thermal comfort | CO | Journal of Building Engineering | Existing natural ventilation control methods in cold climates, especially rule-based CO₂ control, often fail to maintain indoor air quality and thermal comfort in winter. There is also a lack of control-oriented models suitable for MPC implementation in natural ventilation contexts. Furthermore, most studies use simulations (e.g., EnergyPlus) rather than real buildings. | The study proposes a data-driven Model Predictive Control (MPC) strategy for short-term winter natural ventilation using machine learning algorithms. It aims to: 1. Maintain indoor CO₂ below 1000–1200 ppm, 2. Limit thermal discomfort (indoor temp within 20–24 °C), 3. Avoid additional heating energy penalties, 4. Evaluate real-world implementation in a retrofitted smart building. | Subsystem | Indoor air temperature, IAQ | Component | Black-Box | Subspace identification (N4SID) to derive linear predictive models | 1st-order system dynamics | No | - | Yes | Real data | System Identification Toolbox | MATLAB | Real building | A retrofitted 4-floor smart building in Cambridge, MA, USA, with 365 m² floor area and 300+ sensors. | - | - | - | - | - | - | - | - | - | - | - | Weather station, Hugo Muller GS 40.10 knx, Hugo Muller FU 40.00 knx, Casella 178031C, Casella 178035C, Siemens UP 258E22, Siemens UP258E22 (occupant sensor), BTU meter | 5min | Window opening percentage | Low | CO₂ concentration, Indoor temperature, Energy consumption | Rule-based and demand-controlled ventilation strategies | Yes | Full-scale real-world deployment | Yes | Model representation limit | INDOOR AIR-QUALITY; THERMAL COMFORT; PERFORMANCE; SYMPTOMS; SYSTEMS; FLOW | [Zhang, Wei; Malkawi, Ali] Harvard Univ, Ctr Green Bldg & Cities, Cambridge, MA 02138 USA; [Wu, Wentao] Univ Canterbury, Dept Civil & Nat Resources Engn, Christchurch 8140, New Zealand; [Norford, Leslie] MIT, Dept Architecture, Cambridge, MA 02139 USA; [Li, Na] Harvard Univ, Sch Engn & Appl Sci, Cambridge, MA 02138 USA | Harvard University; University of Canterbury; Massachusetts Institute of Technology (MIT); Harvard University | Zhang, W (corresponding author), Harvard Univ, Ctr Green Bldg & Cities, Cambridge, MA 02138 USA. | wei_zhang@g.harvard.edu | 14 | 14 | 73 | [5 empty] | 106602
45 | 45 | Physics-informed hierarchical data-driven predictive control for building HVAC systems to achieve energy and health nexus | Wang, XZ; Dong, B | Wang, Xuezheng; Dong, Bing | 2026-07-15 | 2023 | http://dx.doi.org/10.1016/j.enbuild.2023.113088 | Model predictive control; Physics -informed neural network; Energy reduction; Indoor environmental quality | CO | Energy and Buildings | 1. Lack of scalable, physically consistent dynamic models for predictive control. 2. Most data-driven models are recurrent, suffer from long-horizon degradation, and ignore indoor air quality and system-level energy. 3. Lack of analysis on the impact of weather forecasting uncertainty on predictive control. | 1. Develop a physics-informed, input convex, multi-step neural network to predict indoor temperature and CO₂ concentration. 2. Integrate the model into a two-level hierarchical data-driven predictive control (HDDPC) framework. 3. Optimize both room-level and system-level energy with constraints on thermal comfort and indoor air quality. 4. Quantify the effect of forecast uncertainty on performance. | Subsystem | Indoor air temperature, IAQ | Component | Black-Box | Physics-informed Input Convex Neural Network (ICNN) using masked feedforward ANN architecture | 1. Partial connections enforce temporal causality. 2. Inputs only affect future predictions (no future-to-past leakage). 3. Convexity ensured via non-negative weights and ReLU activations. | No | - | Yes | Real data | N/A | Python | Virtual testbed | Small student office with an AHU and four VAVs (aggregated as one zone). | Building thermal, IAQ | Component | Black-Box | Physics-informed Input Convex Neural Network (ICNN) using masked feedforward ANN architecture | 1. Partial connections enforce temporal causality. 2. Inputs only affect future predictions (no future-to-past leakage). 3. Convexity ensured via non-negative weights and ReLU activations. | No | - | Yes | Real data | N/A | Python | - | 15min | System-level: supply airflow rate, supply air temperature, outdoor airflow rate | Medium | CO₂ concentration, Indoor temperature, Energy consumption | Historical control baseline (default HVAC operation), Ideal vs. forecasted weather scenarios | No | Simulation only | No | The process model and testbed are the same | IMPLEMENTATION; FLEXIBILITY | [Wang, Xuezheng; Dong, Bing] Syracuse Univ, Dept Mech & Aerosp Engn, 263 Link Hall, Syracuse, NY 13244 USA | Syracuse University | Dong, B (corresponding author), Syracuse Univ, Dept Mech & Aerosp Engn, 263 Link Hall, Syracuse, NY 13244 USA. | bidong@syr.edu | 18 | 18 | 291 | [5 empty] | 113088
46 | 46 | Building thermal modeling and model predictive control with physically consistent deep learning for decarbonization and energy optimization | Xiao, TQ; You, FQ | Xiao, Tianqi; You, Fengqi | 2026-07-15 | 2023 | http://dx.doi.org/10.1016/j.apenergy.2023.121165 | Deep Learning; Physics Consistency; Model Predictive Control; Building Energy Efficiency Optimization; Decarbonization | CO | Applied Energy | The study addresses the lack of reliable and generalizable dynamic models that integrate physical consistency into data-driven approaches. Existing black-box models like LSTM suffer from low generalizability and lack of physical interpretability, while physics-informed models (like PiNNs) often lack strict physical consistency or are limited to simple/single-zone cases and neglect humidity dynamics. | The paper introduces a Physically Consistent Deep Learning (PCDL) model for thermal dynamics in multi-zone buildings and applies it in a Model Predictive Control (MPC) framework. It aims to optimize energy efficiency and thermal comfort while ensuring adherence to physical laws. | Whole System | Indoor air temperature, IAQ | Component | Black-Box | Two-layer NN: RNN (for physics-consistent inputs) + LSTM (for other inputs); termed PCDL | Physics consistency definitions based on building thermal laws (e.g., monotonic relationships between heating/cooling and temperature) | No | - (PMV) | Yes | Simulated data | PyTorch | Python | Virtual testbed | Simulated multi-zone office building (Carpenter Hall, Cornell University) modeled in EnergyPlus, 5 thermal zones, with HVAC systems including heating/cooling coils and humidifiers. | Building thermal, IAQ | Component | White-Box | EnergyPlus-based physics simulation | Standardized HVAC behavior, Operation schedule based on ASHRAE standard | Yes | HVAC system | No | None | BCVTB | EnergyPlus | - | 10 min | Heating power, Cooling power, Humidifying power | Medium | PMV, Energy consumption | On/Off controller, SSM-based MPC (RC model), LSTM-based MPC | No | Simulation only | Yes | Model representation limit | INFORMED NEURAL-NETWORKS; COMFORT; SYSTEM; PERFORMANCE; FRAMEWORK | [Xiao, Tianqi; You, Fengqi] Cornell Univ, Syst Engn, Ithaca, NY 14853 USA; [You, Fengqi] Cornell Univ, Robert Frederick Smith Sch Chem & Biomol Engn, Ithaca, NY 14853 USA | Cornell University; Cornell University | You, FQ (corresponding author), Cornell Univ, Syst Engn, Ithaca, NY 14853 USA. | fengqi.you@cornell.edu | 39 | 39 | 342 | [5 empty] | 121165
47 | 47 | Energy saving and indoor temperature control for an office building using tube-based robust model predictive control | Gao, Y; Miyata, S; Akashi, Y | Gao, Yuan; Miyata, Shohei; Akashi, Yasunori | 2026-07-01 | 2023 | http://dx.doi.org/10.1016/j.apenergy.2023.121106 | Model predictive control; Prediction uncertainty; HVAC system management; Tube-based model predictive control | CO | Applied Energy | 1. Traditional MPC for HVAC often assumes perfect predictions or considers unrealistic worst-case scenarios (RMPC) or complicated probabilistic frameworks (SMPC). 2. Existing tube-based MPC applications to HVAC are scarce and do not properly model how uncertainty evolves over time. 3. There’s a need for a robust control approach that better represents real-world prediction uncertainty and mitigates its effects. | 1. Propose and implement a tube-based robust MPC framework tailored for HVAC systems. 2. Improve indoor temperature control and reduce operating costs under uncertain prediction conditions. 3. Modify the uncertainty representation in tube MPC to better reflect real prediction errors that increase over the forecast horizon. 4. Validate the method using the BOPTEST framework under various uncertainty scenarios. | Subsystem | Building thermal | Component | Gray-Box | Resistor–Capacitor (RC) thermal network model (2R2C) | Linear heat transfer | No | - | Yes | Simulated data | N/A | Python | Virtual testbed | BOPTEST's “bestest_air” test case (48 m² office, 2-person occupancy, 4-pipe fan coil unit HVAC, near Denver, CO) | VAV system | Subsystem | White-Box | BOPTEST | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | BOPTEST | Modelica | - | 15min | Supply air temperature, Fan air mass flow rate | Medium | Indoor temperature, Operating cost | Open-loop MPC, Closed-loop MPC | No | Simulation only | Yes | Model representation limit | CONTROL STRATEGIES; SYSTEMS; OPTIMIZATION; PERFORMANCE; SIMULATION; FRAMEWORK | [Gao, Yuan; Miyata, Shohei; Akashi, Yasunori] Univ Tokyo, Grad Sch Engn, Dept Architecture, Tokyo, Japan | University of Tokyo | Gao, Y (corresponding author), Univ Tokyo, Grad Sch Engn, Dept Architecture, Tokyo, Japan. | yuangao1120@gmail.com | 24 | 24 | 341 | [5 empty] | 121106
48 | 48 | Physics-informed neural networks for building thermal modeling and demand response control | Chen, YB; Yang, QG; Chen, Z; Yan, CC; Zeng, S; Dai, MK | Chen, Yongbao; Yang, Qiguo; Chen, Zhe; Yan, Chengchu; Zeng, Shu; Dai, Mingkun | 2026-04-15 | 2023 | http://dx.doi.org/10.1016/j.buildenv.2023.110149 | Physics-informed neural networks; Control-oriented modeling; Grid-integrated buildings; Demand response | EF | Building and Environment | Existing physics-based models are accurate but require intensive customization for each building and are hard to generalize. Purely data-driven models are easier to develop but need large datasets and often lack interpretability and generalization ability. There is a lack of methods that blend the strengths of both for control-oriented modeling in demand response (DR) settings. | The study proposes a new model called PhysCon, which combines physical interpretability (via a 2R2C thermal model) and data-driven learning (via PINNs) to enhance predictive accuracy and response in DR control for buildings. It also evaluates energy flexibility across different internal thermal mass scenarios. | Subsystem | Building thermal | Component | Black-Box | Physics-Informed Neural Networks (PINNs) combining a 2R2C model and a fully connected feedforward neural network. | Solar gain was set to zero due to sun-shading closure. | No | - | Yes | Lab | PyTorch Lightning | Python | Lab | Two 16 m² rooms inside a controlled environmental chamber, one configured for light thermal mass (approx. 185 kg) and the other for heavy thermal mass (approx. 740 kg). HVAC controlled by air-water AC systems, PID valve control, 3-level fan speed. | - | - | - | - | - | - | - | - | - | - | - | ADAM-4118 module, RS-485 serial port, T-type thermocouple thermometer, Calorimeter Shark-773 | 5min | Indoor temperature setpoint | High | Energy saving, Peak load reduction | Compared to conventional data-driven neural networks. | Partial | Lab setup | Yes | Model representation limit | PREDICTIVE CONTROL; COMMERCIAL BUILDINGS; IDENTIFICATION; VALIDATION | [Chen, Yongbao; Yang, Qiguo; Chen, Zhe] Univ Shanghai Sci & Technol, Sch Energy & Power Engn, Shanghai 200093, Peoples R China; [Yan, Chengchu] Nanjing Tech Univ, Coll Urban Construct, Nanjing 210009, Peoples R China; [Zeng, Shu] Univ Shanghai Sci & Technol, Coll Foreign Languages, Shanghai 200093, Peoples R China; [Dai, Mingkun] Tongji Univ, Sch Mech Engn, Shanghai 201804, Peoples R China | University of Shanghai for Science & Technology; Nanjing Tech University; University of Shanghai for Science & Technology; Tongji University | Chen, YB; Yang, QG (corresponding author), Univ Shanghai Sci & Technol, Sch Energy & Power Engn, Shanghai 200093, Peoples R China. | chenyongbao@usst.edu.cn; yangqg@usst.edu.cn | 41 | 41 | 234 | [5 empty] | 110149
49 | 49 | Development of Anomaly Detectors for HVAC Systems Using Machine Learning | Borda, D; Bergagio, M; Amerio, M; Masoero, MC; Borchiellini, R; Papurello, D | Borda, Davide; Bergagio, Mattia; Amerio, Massimo; Masoero, Marco Carlo; Borchiellini, Romano; Papurello, Davide | FEB | 2023 | http://dx.doi.org/10.3390/pr11020535 | HVAC; fault detection and diagnosis; anomaly detection; artificial intelligence; machine learning; energy savings | FDD | Processes | Traditional FDD approaches based on physical modeling (quantitative models) or rule-based systems (qualitative models) are labor-intensive, system-specific, and difficult to generalize. Furthermore, most data-driven models rely heavily on labeled data, which is often scarce or expensive to obtain in real-world HVAC systems. | 1. Develop supervised and semi-supervised models for fault detection and diagnosis (FDD) using limited labeled data. 2. Build predictive models that capture HVAC system dynamics. 3. Create classification models that work on partially labeled datasets. 4.Enable scalable, data-driven FDD with minimal feature engineering. | Component | AHU | Component | Black-Box | Bidirectional Gated Recurrent Unit (BiGRU) neural network as a Multi-Input Multi-Output (MIMO) sequence model (RNN encoder–decoder with sequence prediction). | Seasonal operation (winter only) considered; no cross-seasonal generalization. | No | - | Yes | Real data | Keras, TensorFlow | Python | Historical data | BMS data from an operating building | - | - | - | - | - | - | - | - | - | - | - | - | 15min | - | - | BAS (Balanced Accuracy Score) for classification, Accuracy Score | Classical methods like Vector AutoRegression (VAR) and Random Forest (RF) used as baselines. | No | Historical data | Yes | Model representation limit | FAULT-DETECTION; DIAGNOSIS; OPTIMIZATION; DESIGN | [Borda, Davide; Bergagio, Mattia; Amerio, Massimo] EURIX, Corso Vittorio Emanuele II, 61, I-10128 Turin, Italy; [Borda, Davide; Bergagio, Mattia; Amerio, Massimo; Borchiellini, Romano; Papurello, Davide] Polytech Univ Turin, Energy Ctr Initiat, Via Paolo Borsellino, 38-16, I-10138 Turin, Italy; [Masoero, Marco Carlo; Borchiellini, Romano; Papurello, Davide] Polytech Univ Turin, Dept Energy DENERG, 24 Corso Duca Abruzzi, I-10129 Turin, Italy | Polytechnic University of Turin; Polytechnic University of Turin | Borda, D; Bergagio, M (corresponding author), EURIX, Corso Vittorio Emanuele II, 61, I-10128 Turin, Italy.;Borda, D; Bergagio, M (corresponding author), Polytech Univ Turin, Energy Ctr Initiat, Via Paolo Borsellino, 38-16, I-10138 Turin, Italy. | borda@eurixgroup.com; bergagio@eurixgroup.com | 14 | 14 | 11 | 2 |  |  |  |  | 535
50 | 50 | Dynamic room temperature setpoints of air-conditioning demand response based on heat balance equations with thermal comfort model as constraint: On-site experiment and simulation | Li, ZY; Meng, QL; Wei, YA; Zhang, L; Sun, Z; Lei, Y; Yang, L; Yan, XY | Li, Zeyang; Meng, Qinglong; Wei, Ying'an; Zhang, Liang; Sun, Zhe; Lei, Yu; Yang, Li; Yan, Xiuying | 2026-04-15 | 2023 | http://dx.doi.org/10.1016/j.jobe.2022.105798 | Demand response; Air-conditioning; Heat balance equation; Radial basis function; Temperature setpoint | EF | Journal of Building Engineering | Most demand response (DR) strategies in HVAC systems rely on fixed indoor temperature setpoints or oversimplified assumptions that neglect dynamic thermal behavior and occupant comfort. There is also limited integration of thermal comfort modeling into DR optimization, especially under varying time-of-use (TOU) electricity pricing. | 1. Propose a DR strategy that dynamically optimizes indoor temperature setpoints using a heat balance model constrained by thermal comfort. 2. Develop separate comfort models for DR and non-DR periods based on PMV. 3. Predict outdoor temperature using an RBF neural network to support setpoint planning. 4. Validate the proposed strategy through both real-world experiments and EnergyPlus simulations. | Subsystem | Building thermal | Component | White-Box | Heat balance equations | Uniform indoor and wall temperatures, No internal heat radiation or infiltration | No | - (PMV) | Yes | Real data | N/A | N/A | Real building, Virtual testbed | Yunke Energy Saving Demonstration Building in Shenzhen; four-story commercial office building with Temperature and Humidity Independent Control (THIC) HVAC system. Experiments conducted in west zone of the second floor using thermostats, fan coils, and radiant panels. Virtual: E+ model | Building thermal | Component | White-Box | EnergyPlus-based physics simulation | Standardized E+ modelling | Yes | HVAC system | Yes | Real data | N/A | EnergyPlus | Siemens Programmable Logic Controller (PLC) (S7 200 CPU), Ethernet module, Switches, Weather station, Temperature and humidity sensor, CO2 sensor | 1h | Indoor temperature setpoint | High | Energy savings, Cost savings, Comfort level (PMV/PPD within target ranges) | Fixed setpoint strategy | Yes | Full-scale real-world deployment | Yes, No | Model representation limit | ADAPTIVE COMFORT; ENERGY DEMAND; BUILDINGS | [Li, Zeyang; Meng, Qinglong; Wei, Ying'an; Zhang, Liang; Sun, Zhe; Yang, Li] Changan Univ, Sch Civil Engn, Xian 710061, Peoples R China; [Lei, Yu] China Construct Third Engn Bur Installat Engn Co L, Wuhan 430040, Peoples R China; [Yan, Xiuying] Xian Univ Architecture & Technol, Xian 710055, Peoples R China | Chang'an University; Xi'an University of Architecture & Technology | Meng, QL (corresponding author), Changan Univ, Sch Civil Engn, Xian 710061, Peoples R China. | mengqinglong@chd.edu.cn | 14 | 15 | 65 | [5 empty] | 105798
51 | 51 | Energy Consumption Optimization for Heating, Ventilation and Air Conditioning Systems Based on Deep Reinforcement Learning | Peng, Y; Shen, HJ; Tang, XC; Zhang, SZ; Zhao, JX; Liu, YR; Nie, YM | Peng, Yi; Shen, Haojun; Tang, Xiaochang; Zhang, Sizhe; Zhao, Jinxiao; Liu, Yuru; Nie, Yuming |  | 2023 | http://dx.doi.org/10.1109/ACCESS.2023.3305683 | HVAC systems; DDPG; deep reinforcement learning; energy consumption | CO | IEEE Access | Traditional HVAC control methods rely on complex physical modeling and cannot efficiently handle nonlinear, coupled, and time-varying behaviors. Moreover, existing DRL-based methods either lack flexibility or robustness due to poor simulation fidelity or inefficient training strategies. | 1. Propose a CNN–LSTM-based energy consumption prediction model for HVAC systems to simulate dynamic behavior. 2. Develop an enhanced DDPG (E-DDPG) algorithm to optimize HVAC energy consumption based on this model. 3. Improve training strategies using up/down sampling and dynamic delayed updates to enhance robustness and efficiency. | Subsystem | Chiller | Component | Black-Box | CNN–LSTM neural network | Feature selection reduces inputs to four dominant sensor variables | No | - | Yes | Real data | PyTorch | Python | Virtual testbed | Virtual environment created using a CNN–LSTM model trained on real operational data from five HVAC plants (multiple geographical locations). | Chiller | Component | Black-Box | CNN–LSTM neural network | Feature selection reduces inputs to four dominant sensor variables | No | - | Yes | Real data | N/A | Python | - | 30s | N/A | - | Energy Efficiency Ratio (EER) improvement, Training time, convergence iterations, and EER fluctuation stability | Baseline neural networks: LSTM, GRU, CNN, DRL algorithm: PPO (Proximal Policy Optimization) | No | Simulation only | No | The process model (environment) and testbed are the same | COMFORT | [Peng, Yi; Shen, Haojun] China Univ Petr, Coll Oceanog & Space Informat, Qingdao 266580, Peoples R China; [Tang, Xiaochang; Zhang, Sizhe; Zhao, Jinxiao; Liu, Yuru; Nie, Yuming] China Univ Petr, Coll Comp Sci & Technol, Qingdao 266580, Peoples R China | China University of Petroleum; China University of Petroleum | Peng, Y (corresponding author), China Univ Petr, Coll Oceanog & Space Informat, Qingdao 266580, Peoples R China. | 2016020219@s.upc.edu.cn | 12 | 12 | 11 |  |  |  | 88265 | 88277
52 | 52 | A Control Framework to Enable a Commercial Building HVAC System for Energy and Regulation Market Signal Tracking | Wang, WY; Tian, GY; Sun, QZ; Liu, HR | Wang, Wenyi; Tian, Guanyu; Sun, Qun Zhou; Liu, Hongrui | JAN | 2023 | http://dx.doi.org/10.1109/TPWRS.2022.3156867 | HVAC; Fans; Atmospheric modeling; Buildings; Cooling; Mathematical models; Water heating; Commercial building HVAC system; two-level control; energy and regulation market signal tracking; control-oriented model; Dymola high fidelity model | EF | IEEE Transactions on Power Systems | Existing control methods for HVAC-based demand response often focus solely on fan control for frequency regulation, overlooking the interdependent impact on water-loop components (chiller and pumps). This can result in inaccurate grid signal tracking, especially when entire HVAC systems participate in regulation markets. | 1. Develop a complete HVAC control-oriented model incorporating chiller, pumps, AHUs, and their interdependencies. 2. Propose a two-level control framework: First level: 5-minute nonlinear MPC for energy market signal tracking. Second level: 4-second control for frequency regulation via fan-only control. 3. Validate this strategy via high-fidelity Dymola model and co-simulation with MATLAB. | Whole System | Building thermal, HX | Component | White-Box | Energy balance equations (mass and energy conservation), All models combined into one discretized state-space model for control purpose | Uniform room temperature distribution, Simplified counterflow cooling coil. | Yes | Power, Air mixing | Yes | Simulated data | IPOPT | MATLAB | Virtual testbed | High-fidelity model in Dymola using the Modelica Buildings Library. Two AHUs, one chiller, and one pump. | HVAC system | Whole System | White-Box | Component-based physical modeling (Modelica standard components) | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | Modelica Buildings Library, BCVTB | Modelica | - | 5-minute interval for energy market tracking, 4-second interval for frequency regulation control | Chilled water mass flow rate, Chilled water supply temperature, Air mass flow rate, Damper opening | Low, Medium | Indoor temperature, Chiller COP, Smoothness of fan and pump operation | Benchmark model: simplified model with fixed water-loop settings; Benchmark control: conventional PI-based control | No | Simulation only | Yes | The control-oriented model simplifies some physical behaviors | FREQUENCY REGULATION; MODEL; LOAD | [Wang, Wenyi; Tian, Guanyu; Sun, Qun Zhou] Univ Cent Florida, Dept Elect & Comp Engn, Orlando, FL 32816 USA; [Liu, Hongrui] San Jose State Univ, Dept Ind & Syst Engn, San Jose, CA 95192 USA | State University System of Florida; University of Central Florida; California State University System; San Jose State University | Sun, QZ (corresponding author), Univ Cent Florida, Dept Elect & Comp Engn, Orlando, FL 32816 USA. | we857643@ucf.edu; tiang@knights.ucf.edu; qz.sun@ucf.edu; hongrui.liu@sjsu.edu | 12 | 13 | 38 | 1 |  |  | 290 | 301
53 | 53 | Model predictive control of indoor thermal environment conditioned by a direct expansion air conditioning system | Xia, YD; Zhu, M; Jiang, AP; Wang, J; Bai, XX; Deng, SM | Xia, Yudong; Zhu, Ming; Jiang, Aipeng; Wang, Jian; Bai, Xiaoxia; Deng, Shiming | MAR | 2023 | http://dx.doi.org/10.1007/s12273-022-0949-1 | direct expansion air conditioning; humidity control; model predictive control; variable speed; operational efficiency | CO | Building Simulation | 1. Existing controllers for DX A/C systems focus primarily on minimizing temperature and humidity tracking errors without considering the impact of compressor and fan speeds on energy consumption. 2. Most MPC strategies in literature focus on chilled-water systems and neglect latent heat effects or application to DX systems. | 1. Develop an MPC strategy for a variable-speed DX A/C system that simultaneously controls air temperature and humidity while improving energy efficiency. 2. Formulate and validate a physically-based nonlinear model considering both sensible and latent heat transfers. 3. Compare the MPC performance with LQG control in terms of control accuracy and energy savings. | Subsystem | DX A/C system | Subsystem | White-Box | Linearized model obtained through Taylor series expansion around a steady-state operating point. | Lumped air volume with ideal mixing, Segmented wet/dry zones in evaporator, Constant condensing pressure and evaporator superheat, 95% RH air leaving evaporator, Negligible losses in ductwork. | No | - | Yes | Lab | quadprog | MATLAB | Virtual testbed | Original nonlinear model | DX A/C system | Subsystem | White-Box | Energy conservation laws, Moisture balance equations, Heat and mass transfer physics | Lumped air volume with ideal mixing, Segmented wet/dry zones in evaporator, Constant condensing pressure and evaporator superheat, 95% RH air leaving evaporator, Negligible losses in ductwork. | No | - | Yes | Lab | REFPROP | MATLAB | - | 10s | Compressor speed, supply fan speed | Low | Indoor temperature and humidity tracking error (IAE), Energy consumption | Linear-Quadratic-Gaussian (LQG) controller | No | Simulation only | Yes | Model representation limit: linearization | INHERENT OPERATIONAL CHARACTERISTICS; FUZZY-LOGIC CONTROLLER; VARIABLE-SPEED; HUMIDITY CONTROL; MULTIVARIABLE CONTROL; CAPACITY CONTROLLER; CONTROL ALGORITHMS; HUMAN HEALTH; HEAT-PUMP; A/C UNIT | [Xia, Yudong; Zhu, Ming; Jiang, Aipeng; Wang, Jian] Hangzhou Dianzi Univ, Sch Automat, Sch Artificial Intelligence, Hangzhou, Peoples R China; [Bai, Xiaoxia] Hong Kong Polytech Univ, Dept Bldg Environm & Energy Engn, Hong Kong, Peoples R China; [Deng, Shiming] Qatar Univ, Dept Mech & Ind Engn, Doha, Qatar | Hangzhou Dianzi University; Hong Kong Polytechnic University; Qatar University | Jiang, AP (corresponding author), Hangzhou Dianzi Univ, Sch Automat, Sch Artificial Intelligence, Hangzhou, Peoples R China. | jiangaipeng@hdu.edu.cn | 14 | 14 | 16 | 3 |  |  | 357 | 378
54 | 54 | Trade-off decisions in a novel deep reinforcement learning for energy savings in HVAC systems | Dawood, SM; Hatami, A; Homod, RZ | Dawood, Suroor M.; Hatami, Alireza; Homod, Raad Z. | 2026-11-02 | 2022 | http://dx.doi.org/10.1080/19401493.2022.2099465 | Heating; ventilating; and air conditioning (HVAC) systems; Energy saving; Reinforcement learning; Nonlinear autoregressive exogenous neural network (NARX-NN) | CO | Journal of Building Performance Simulation | Most prior RL-based HVAC studies focus on minimizing energy consumption or cost while maintaining thermal comfort, but rarely consider indoor CO₂ concentration as part of occupant comfort. Additionally, many use model-free RL approaches that are data-hungry and less efficient for control tasks. | 1. Develop a model-based deterministic policy RL (DP-RL) controller. 2. Propose a hybrid model-based deep RL controller (DP-NARX-RL) using a nonlinear autoregressive exogenous neural network (NARX-NN). 3.Simultaneously minimize HVAC energy use and maintain indoor temperature & CO₂ levels. | Subsystem | AHU, Indoor air temperature, IAQ | Subsystem | White-Box | Thermodynamic energy balance, Mass conservation for CO₂, Transfer function modeling in Laplace domain | Latent heat neglected, Fixed number of occupants, Deterministic, linearized model structure | No | - | No | None | N/A | MATLAB | Virtual testbed | Same as application | AHU, Indoor air temperature, IAQ | Subsystem | White-Box | Thermodynamic energy balance, Mass conservation for CO₂, Transfer function modeling in Laplace domain | Latent heat neglected, Fixed number of occupants, Deterministic, linearized model structure | No | - | No | None | N/A | MATLAB | - | Case 1: 15 minutes, Case 2: 4 minutes | Chilled water valve position, Air damper position (fresh/return), Lighting (on/off), Windows (open/close) | Low | Energy consumption, Energy cost, Stability of indoor temperature and CO₂ | Standard RL controller, PID controller (case study 2) | No | Simulation only | No | The process model (environment) and testbed are the same | MODEL-PREDICTIVE CONTROL; MANAGEMENT; SMART | [Dawood, Suroor M.; Hatami, Alireza] Bu Ali Sina Univ, Dept Elec Engn, Mahdieh St, Hamadan 6517838695, Hamadan, Iran; [Dawood, Suroor M.] Basrah Univ Oil & Gas, Dept Chem Engn & Oil Refining, Basrah 61004, Iraq; [Homod, Raad Z.] Basrah Univ Oil & Gas, Dept Oil & Gas Eng, Basrah 61004, Iraq | Bu Ali Sina University; Basrah University for Oil & Gas; Basrah University for Oil & Gas | Hatami, A (corresponding author), Bu Ali Sina Univ, Dept Elec Engn, Mahdieh St, Hamadan 6517838695, Hamadan, Iran. | hatamisharif@basu.ac.ir | 20 | 20 | 15 | 6 |  |  | 809 | 831
55 | 55 | A Model Predictive Control for Heat Supply at Building Thermal Inlet Based on Data-Driven Model | Ma, LD; Huang, YY; Zhang, JY; Zhao, TY | Ma, Liangdong; Huang, Yangyang; Zhang, Jiyi; Zhao, Tianyi | NOV | 2022 | http://dx.doi.org/10.3390/buildings12111879 | model predictive control; district heating system; data-driven; long short-term memory | CO | Buildings | Traditional control strategies in district heating systems (DHS) like on–off and PID control suffer from hysteresis and cannot adequately handle the dynamic interaction between pipe networks and building envelopes. Existing MPC approaches often lack robustness or are limited by static modeling paradigms. | 1. Propose a novel data-driven MPC for regulating flow at the building thermal inlet. 2. Develop an LSTM-based indoor temperature prediction model. 3. Optimize flow rates using Particle Swarm Optimization (PSO) to improve thermal comfort and reduce energy consumption. | Subsystem | Indoor air temperature | Component | Black-Box | Long Short-Term Memory (LSTM) neural network | The indoor temperature dynamics are primarily affected by outdoor meteorological parameters, supply/return water temperatures, and historical IAT values. | No | - | Yes | Real data | N/A | MATLAB | Virtual testbed | Simulation performed using real data from 3 buildings in Dalian, China (teaching and office buildings, all using vertical single-pipe DHS); | Indoor air temperature | Component | Black-Box | Long Short-Term Memory (LSTM) neural network | The indoor temperature dynamics are primarily affected by outdoor meteorological parameters, supply/return water temperatures, and historical IAT values. | No | - | Yes | Real data | N/A | MATLAB | - | 1h | Water flow rate | Medium | Temperature tracking accuracy, Response time to temperature setpoint change | Subspace Model Identification (SMI) for prediction accuracy, PID control | No | Simulation only | No | The process model and testbed are the same | PUBLIC BUILDINGS; HVAC SYSTEMS; ENERGY; TEMPERATURE; OPTIMIZATION; PERFORMANCE; NETWORK; MPC | [Ma, Liangdong; Huang, Yangyang; Zhang, Jiyi; Zhao, Tianyi] Dalian Univ Technol, Fac Infrastruct Engn, Dalian 116024, Peoples R China | Dalian University of Technology | Zhao, TY (corresponding author), Dalian Univ Technol, Fac Infrastruct Engn, Dalian 116024, Peoples R China. | zhaotianyi@dlut.edu.cn | 9 | 9 | 12 | 11 |  |  |  |  | 1879
56 | 56 | Model predictive control for multi-zone Variable Air Volume systems based on artificial neural networks | Wei, D; Ma, JM; Jiao, HY; Ran, YB | Wei, Dong; Ma, Jianmin; Jiao, Huanyan; Ran, Yibing | OCT | 2022 | http://dx.doi.org/10.1016/j.jprocont.2022.08.014 | Model predictive control; Neural networks; Cascade control; Variable air volume systems; Building energy efficiency | CO | Journal of Process Control | Traditional VAV systems rely heavily on PID control, which lacks the ability to handle nonlinearities, uncertainties, and couplings in HVAC systems. There is a need for a robust and efficient control approach that minimizes computational burden while enhancing system performance. | 1. Develop an ANN-based MPC framework for zone temperature and duct air volume control in VAV systems. 2. Reduce energy consumption and temperature fluctuations. 3. Improve control robustness and reduce commissioning efforts compared to traditional PID methods. | Subsystem | Indoor air temperature, Air distribution system | Subsystem | Black-Box | Artificial Neural Network (ANN), trained via Bayesian Regularization and Lagrange Variational Approach (LVA) | Assumes input-output data can generalize system dynamics | No | - | Yes | Real data | N/A | MATLAB | Virtual testbed | Two-zone VAV system (graduate studio and office) in a laboratory building at Beijing University of Civil Engineering and Architecture, including AHUs, VAV boxes, fans, sensors (temperature, CO₂, pressure), and dampers. | Indoor air temperature, Air distribution system | Subsystem | Black-Box | Artificial Neural Network (ANN), trained via Bayesian Regularization and Lagrange Variational Approach (LVA) | Assumes input-output data can generalize system dynamics | No | - | Yes | Real data | N/A | MATLAB | - | 5min | Air flow rate setpoint for VAV boxes, Fan voltage | Medium, Low | Temperature oscillation reduction, Energy savings | Cascade PI control | No | Simulation only | No | The process model and testbed are the same | SWITCHED NONLINEAR-SYSTEMS; HVAC SYSTEM; MPC; OPTIMIZATION; BUILDINGS | [Wei, Dong; Ma, Jianmin; Jiao, Huanyan] Beijing Univ Civil Engn & Architecture, Sch Elect & Informat Engn, Beijing, Peoples R China; [Wei, Dong] Beijing Key Lab Intelligent Proc Bldg Big Data, Beijing, Peoples R China; [Ran, Yibing] Siemens China, Beijing, Peoples R China | Beijing University of Civil Engineering & Architecture; Siemens AG; Siemens China | Ran, YB (corresponding author), Siemens China, Beijing, Peoples R China. | weidong@bucea.edu.cn; 2108550020049@stu.bucea.edu.cn; jiaohuanyan@foxmail.com; yibing.ran@siemens.com | 8 | 9 | 118 |  |  |  | 185 | 201
57 | 57 | A predictive control approach for thermal energy management in buildings | Berouine, A; Ouladsine, R; Bakhouya, M; Essaaidi, M | Berouine, Anass; Ouladsine, Radouane; Bakhouya, Mohamed; Essaaidi, Mohamed | NOV | 2022 | http://dx.doi.org/10.1016/j.egyr.2022.07.037 | Building energy management system; Building thermal model; HVAC systems; Occupants? comfort; Energy efficiency; Model predictive control | CO | Energy Reports | Conventional HVAC controllers (e.g., On–Off, PID) do not effectively optimize energy consumption or ensure thermal comfort under dynamic, time-varying environmental conditions. Many MPC implementations rely on complex BES software (e.g., EnergyPlus), which are computationally expensive and thus impractical for real-time applications. | To develop a computationally efficient, real-time Model Predictive Control (MPC) strategy for a single-zone AC system using a simplified white-box thermal model, with the aim of improving energy efficiency and thermal comfort. The study includes simulation-based validation and outlines a Hardware-in-the-Loop (HIL) implementation for future deployment. | Subsystem | Building thermal | Component | White-Box | Physics-based heat balance using ODEs, linearized to a discrete-time state–space model for MPC. | Perfect model (no modeling error); No thermal interaction with adjacent zones; No air exchange or humidity dynamics; No internal gains from occupants; No wind speed effects | No | - | No | None | N/A | MATLAB | Virtual testbed | Simulated single-zone office room | Building thermal | Component | White-Box | Physics-based heat balance using ODEs, linearized to a discrete-time state–space model for MPC. | Perfect model (no modeling error); No thermal interaction with adjacent zones; No air exchange or humidity dynamics; No internal gains from occupants; No wind speed effects | No | - | No | None | N/A | MATLAB | - | 15min | AC heating/cooling power | Medium | Indoor temperature, Power consumption, Peak demand ,Energy savings | Conventional On–Off controller | No | Simulation only | No | The process model and testbed are the same | AIR-CONDITIONING SYSTEM; OCCUPANT BEHAVIOR; HVAC SYSTEM; MODEL; COMFORT; SIMULATION; OPTIMIZATION; IMPLEMENTATION; TEMPERATURE; STRATEGIES | [Berouine, Anass; Ouladsine, Radouane; Bakhouya, Mohamed] Int Univ Rabat, Coll Engn & Architecture, LERMA Lab, Sala El Jadida 11100, Morocco; [Berouine, Anass; Essaaidi, Mohamed] Mohamed V Univ, ENSIAS, Rabat 10713, Morocco | Universite Internationale de Rabat; Mohammed V University in Rabat | Berouine, A (corresponding author), Int Univ Rabat, Coll Engn & Architecture, LERMA Lab, Sala El Jadida 11100, Morocco. | anass.berouine@uir.ac.ma; mohamed.bakhouya@uir.ac.ma; essaaidi@ieee.org | 15 | 15 | 8 |  |  |  | 9127 | 9141
58 | 58 | Site demonstration and performance evaluation of MPC for a large chiller plant with TES for renewable energy integration and grid decarbonization | Kim, D; Wang, Z; Brugger, J; Blum, D; Wetter, M; Hong, TZ; Piette, MA | Kim, Donghun; Wang, Zhe; Brugger, James; Blum, David; Wetter, Michael; Hong, Tianzhen; Piette, Mary Ann | 2026-09-01 | 2022 | http://dx.doi.org/10.1016/j.apenergy.2022.119343 | MPC demonstration; Building optimal control; Model predictive control; District energy system; Carbon reduction; Renewable energy | EF | Applied Energy | While many studies apply Model Predictive Control (MPC) for thermal energy storage (TES) systems, most are simulation-based and do not demonstrate actual on-site performance, especially for large-scale district systems. There's also limited evidence on how MPCs can directly reduce CO₂ emissions in real deployments. | 1. Demonstrate MPC in a real-world, large-scale central chiller plant with TES and PV integration. 2. Evaluate on-site MPC performance in terms of PV self-consumption, CO₂ emissions, and peak electricity demand. 3. Share lessons learned and barriers to large-scale MPC deployment. | Subsystem | TES | Component | Gray-Box | RC thermal network for TES (tank modeled with resistance-capacitance) | TES modeled as a stratified tank with two-layer uniform temperature | No | - | Yes | Real data | GLPK | Python | Real building | Central cooling plant at UC Merced; 5 chillers (total 17.6 MW) serving ~40 buildings; 2 million gallon stratified chilled water tank; Integrated with 4 MW PV array and sophisticated EMS; Nine cooling towers, five condenser pumps, variable-speed secondary pumps | - | - | - | - | - | - | - | - | - | - | - | SOAP (Simple Object Access Protocol), EMS, suds python library, NOAA (National Oceanic and Atmospheric Administration) API, pvlib, MOER, WattTime API | 1h | Primary water flow rate setpoint, Plant mode (chiller configuration) | Low, Medium | PV self-consumption ratio, CO₂ emissions reduction, Peak electricity demand, Utility cost savings | Historical baseline using rule-based storage-priority control (nighttime charging, daytime discharging) | Yes | Full-scale real-world deployment | Yes | Model representation limit | MODEL-PREDICTIVE CONTROL; THERMAL MASS; ICE-STORAGE; ALGORITHMS; OPERATION; ROBUST | [Kim, Donghun; Wang, Zhe; Blum, David; Wetter, Michael; Hong, Tianzhen; Piette, Mary Ann] Lawrence Berkeley Natl Lab, Bldg Technol & Urban Syst Div, Berkeley, CA 94720 USA; [Wang, Zhe] Hong Kong Univ Sci & Technol, Hong Kong, Peoples R China; [Brugger, James] Univ Calif Merced, Merced, CA USA | United States Department of Energy (DOE); Lawrence Berkeley National Laboratory; Hong Kong University of Science & Technology; University of California System; University of California Merced | Kim, D (corresponding author), Lawrence Berkeley Natl Lab, Bldg Technol & Urban Syst Div, Berkeley, CA 94720 USA. | donghunkim@lbl.gov | 39 | 42 | 321 | [5 empty] | 119343
59 | 59 | Model predictive control for the performance improvement of air source heat pump heating system via variable water temperature difference | Wang, WY; Hu, B; Wang, RZ; Luo, MW; Zhang, GP; Xiang, B | Wang, Wenyi; Hu, Bin; Wang, R. Z.; Luo, Mingwen; Zhang, Guangpeng; Xiang, Bo | JUN | 2022 | http://dx.doi.org/10.1016/j.ijrefrig.2022.03.001 | Air source heat pump; Model predictive control; Variable water temperature difference; Data-driven model; Optimization | CO | International Journal of Refrigeration | Traditional Proportional-Integral (PI) control strategies in Air Source Heat Pump (ASHP) systems do not effectively exploit the flexibility offered by variable frequency drives (VFDs), leading to suboptimal energy performance under varying real-world conditions. Specifically, fixed supply-return temperature differences cannot ensure minimal power consumption in varying ambient and load conditions. | 1. Propose a nonlinear Model Predictive Control (MPC) strategy to improve the operating performance of an ASHP heating system. 2. Develop a control-oriented dynamic model using machine learning based on high-fidelity simulation data to drive the MPC. 3. Demonstrate energy savings over conventional PI control through simulation under multiple test scenarios. | Subsystem | ASHP | Subsystem | Black-Box | Data-driven nonlinear regression using sparse identification from simulation-generated data | Return water temperature is treated as an external disturbance. Compressor and water pump are main controllable components; evaporator fan is constant-speed. | Yes | Water pump power | Yes | Simulated data | N/A | N/A | Virtual testbed | High-fidelity physics-based ASHP model built in Dymola | ASHP | Subsystem | White-Box | Modular thermodynamic simulation with component-level dynamics | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | TIL Suite | Modelica | - | 1h | Water mass flow rate, Compressor frequency | Low | Total power consumption, Energy savings, Heating capacity maintenance | Conventional PI control with fixed 5°C supply-return temperature difference | No | Simulation only | Yes | Model representation limit | COMPRESSOR | [Wang, Wenyi; Hu, Bin; Wang, R. Z.] Shanghai Jiao Tong Univ, Inst Refrigerat & Cryogen, Res Ctr Solar Power & Refrigerat MOE China, Shanghai 200240, Peoples R China; [Luo, Mingwen; Zhang, Guangpeng; Xiang, Bo] Guangdong Midea HVAC Equipment Co Ltd, Foshan 528311, Guangdong, Peoples R China | Shanghai Jiao Tong University; Midea | Hu, B (corresponding author), Shanghai Jiao Tong Univ, Inst Refrigerat & Cryogen, 800 Dongchuan Rd, Shanghai 200240, Peoples R China. | hb1223@sjtu.edu.cn | 18 | 19 | 138 |  |  |  | 169 | 179
60 | 60 | Virtual Hardware-in-the-Loop FMU Co-Simulation Based Digital Twins for Heating, Ventilation, and Air-Conditioning (HVAC) Systems | Abrazeh, S; Mohseni, SR; Zeitouni, MJ; Parvaresh, A; Fathollahi, A; Gheisarnejad, M; Khooban, MH | Abrazeh, Saber; Mohseni, Saeid-Reza; Zeitouni, Meisam Jahanshahi; Parvaresh, Ahmad; Fathollahi, Arman; Gheisarnejad, Meysam; Khooban, Mohammad-Hassan | FEB | 2023 | http://dx.doi.org/10.1109/TETCI.2022.3168507 | HVAC; Digital twins; Control systems; MIMO communication; Humidity; Backstepping; Space heating; Heating; ventilating and air-conditioning (HVAC); deep reinforcement learning (DRL); nonlinear integral-backstepping (NIB); digital twin; hardware-in-loop (HIL) | CO | IEEE Transactions on Emerging Topics in Computational Intelligence | The study addresses the lack of real-time adaptive control strategies that can accurately replicate and predict HVAC system behavior under nonlinear, multi-input multi-output (MIMO) conditions. It also responds to the limitations of model-based methods that require system identification and are often not robust to real-world implementation noise. | 1. Develop a model-free nonlinear integral backstepping (NIB) control strategy tuned using Proximal Policy Optimization (PPO). 2. Create a digital twin-based control architecture using Hardware-in-the-Loop (HIL) and Software-in-the-Loop (SIL) platforms. 3. Reduce the mismatch between SIL and HIL system outputs for humidity and temperature regulation. 4. Validate the framework through co-simulation using Functional Mockup Interface (FMI) standards and Functional Mockup Units (FMUs). | Subsystem | Indoor air temperature, IAQ, HX | Subsystem | White-Box | Nonlinear bilinear model; equations include heat and mass balance with augmented states and decoupling control. | Bilinear behavior of HVAC dynamics. | No | - | No | None | N/A | MATLAB | HIL | HIL: LANCHXL-F28379D C2000 TI Microcontroller used to emulate hardware, including small faults and delays. | Indoor air temperature, IAQ, HX | Subsystem | White-Box | Nonlinear bilinear model; equations include heat and mass balance with augmented states and decoupling control. | Bilinear behavior of HVAC dynamics. | No | - | No | None | FMI, Simulink | MATLAB | N/A | N/A | Air flow rate and water flow rate | Medium | Humidity and temperature tracking error, Settling time, Overshoot and undershoot | Backstepping and PID controllers. | Partial | HIL | No | The process model (environment) and testbed are the same | ADAPTIVE CONTROLLER; NONLINEAR CONTROL; LEARNING CONTROL; COMFORT | [Abrazeh, Saber; Parvaresh, Ahmad] Univ Zagreb, Fac Elect Engn & Comp, Zagreb 10000, Croatia; [Mohseni, Saeid-Reza] Sharif Univ Technol, Tehran 1458889694, Iran; [Zeitouni, Meisam Jahanshahi] Shiraz Univ Technol, Shiraz 7155713876, Iran; [Fathollahi, Arman] Shahrekord Univ, Fac Engn & Technol, Dept Elect Engn, Shahrekord 64165478, Iran; [Gheisarnejad, Meysam; Khooban, Mohammad-Hassan] Aarhus Univ, Dept Elect & Comp Engn, DK-8200 Aarhus, Denmark | University of Zagreb; Sharif University of Technology; Shiraz University of Technology; Shahrekord University; Aarhus University | Gheisarnejad, M (corresponding author), Aarhus Univ, Dept Elect & Comp Engn, DK-8200 Aarhus, Denmark. | saber.abrazeh@yahoo.com; sr.mohseni@alum.sharif.edu; jahanshahi.meisam@gmail.com; parvaresh.atunad@yahoo.com; a.fattollahi@yahoo.com; me.gheisarnejad@gmail.com; mhkhoban@gmail.com | 14 | 15 | 7 | 1 |  |  | 65 | 75
61 | 61 | Transactive control of air-conditioning systems in buildings for participation in Singapore's Demand Response market through load curtailment | Chandra, R; Radhakrishnan, KK; Panda, SK | Chandra, Rohit; Radhakrishnan, Krishnanand Kaippilly; Panda, Sanjib Kumar | SEP | 2022 | http://dx.doi.org/10.1016/j.segan.2022.100742 | Transactive control; Demand response; Central air conditioning; Buildings | EF | Sustainable Energy, Grids and Networks | Prior HVAC-based demand response (DR) controls were often static, lacked dynamic considerations (like cooling load carryover), and were not integrated with accurate building energy models. There was also a need for scalable, occupant-aware DR control strategies that can be applied using existing BEM tools. | 1. Propose a novel Transactive Energy (TE) based virtual market for zone-level bidding of conditioned air. 2. Use dynamic programming (DP) for multi-step occupant comfort-driven bidding strategies. 3. Integrate EnergyPlus-based detailed ACMV modeling for accurate DR bid formation. 4. Validate DR participation benefits (cost savings and revenue) through co-simulation with real market signals from Singapore. | Whole System | Indoor air temperature | Component | Black-Box | Linear regression-based thermal models for zones using EnergyPlus output data | Linear zone thermal response to outdoor temperature, occupancy, equipment load, and cooling effort, No inter-zone thermal interactions | No | - | Yes | Simulated data | Statistics and Machine Learning Toolbox | MATLAB | Virtual testbed | EnergyPlus "Small Office Building" model with 5 zones (VAVs) and central AHU/chiller; tropicalized for Singapore conditions. | Building thermal | Component | White-Box | Detailed envelope models from EnergyPlus | High-fidelity model, no major simplifying assumptions beyond library defaults. | Yes | Chiller, AHU, Pump | Yes | Validated platform | N/A | EnergyPlus | - | 1h | Conditioned air flow rate (per zone) | Medium | DR quantity (LCQ), electricity cost savings, DR revenue, occupant discomfort | Baseline (comfort-only control), One-step bidding, Hao et al. (2017) | No | Simulation only | Yes | Model representation limit | PRICE | [Chandra, Rohit; Panda, Sanjib Kumar] Natl Univ Singapore, Dept Elect & Comp Engn, Singapore 119077, Singapore; [Radhakrishnan, Krishnanand Kaippilly] Berkeley Educ Alliance Res Singapore, CREATE Tower,1 Create Way,11-00, Singapore 138602, Singapore | National University of Singapore | Chandra, R (corresponding author), Natl Univ Singapore, Dept Elect & Comp Engn, Singapore 119077, Singapore. | rohitchandra@u.nus.edu | 10 | 12 | 31 | [5 empty] | 100742
62 | 62 | Investigation of the effect of the envelope on building thermal storage performance under model predictive control by dynamic pricing | Wei, ZC; Calautit, J | Wei, Zhichen; Calautit, John | MAY | 2022 | http://dx.doi.org/10.1016/j.segy.2022.100068 | Thermal storage; Demand response; Model predictive control (MPC); Building renovation | EF | Smart Energy | While some studies assessed the effect of building envelope (particularly thermal mass and insulation) on energy shifting under dynamic pricing, they often relied on setpoint-based control strategies that did not fully account for thermal response delays—especially problematic with floor heating (FH) systems. This could result in comfort violations like overheating in lightweight constructions. | To compare the energy shifting performance of lightweight vs. heavyweight building envelopes under a Model Predictive Control (MPC) strategy that explicitly accounts for building thermal dynamics. The study evaluates how thermal mass impacts demand response performance and energy cost savings under dynamic pricing. | Component | Building thermal | Component | Gray-Box | RC model developed based on physical heat transfer principles with parameters tuned using TRNSYS data. | Lumped air volume with ideal mixing | No | - | Yes | Simulated data | N/A | MATLAB | Virtual testbed | TRNSYS-based simulation of a single-zone building in London with floor heating and variable wall mass (lightweight vs. heavyweight) | Building thermal | Component | White-Box | Physics-based simulation via TRNSYS layers | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | N/A | TRNSYS | - | 15min | Heating system ON/OFF | Low | Electricity cost, Comfort violation percentage, Energy consumption, Shifting of energy use to low-price periods | Rule-based on/off controller | No | Simulation only | Yes | Model representation limit | FLOOR HEATING-SYSTEM; DEMAND-SIDE MANAGEMENT; ENERGY FLEXIBILITY; LOAD; GENERATION; INTEGRATION; COMMITMENT; IMPACT; MASS | [Wei, Zhichen; Calautit, John] Univ Nottingham, Dept Architecture & Built Environm, Nottingham, England | University of Nottingham | Wei, ZC (corresponding author), Univ Nottingham, Dept Architecture & Built Environm, Nottingham, England. | zhichen.wei@nottingham.ac.uk; john.calautit1@nottingham.ac.uk | 9 | 9 | 6 | [5 empty] | 100068
63 | 63 | Modeling and control of central air conditionings for providing regulation services for power systems | Xie, K; Hui, HX; Ding, Y; Song, YH; Ye, CJ; Zheng, WD; Ye, SQ | Xie, Kang; Hui, Hongxun; Ding, Yi; Song, Yonghua; Ye, Chengjin; Zheng, Wandong; Ye, Shuiquan | 2026-06-01 | 2022 | http://dx.doi.org/10.1016/j.apenergy.2022.119035 | Central air conditioning; Thermal-electrical model; Quantitative assessment; Control strategy; Regulation services | EF | Applied Energy | Traditional power system regulation relies on generation-side flexibility, which is becoming insufficient due to increased penetration of renewable energy. While Central Air Conditionings (CACs) offer high potential for demand-side flexibility, existing methods for quantifying and controlling their regulation capacity are either overly simplistic (e.g., based on room area or temperature reset) or lack precise control at the system level. | 1. Propose a thermal-electrical dynamic model for CACs. 2. Develop a quantitative assessment method for regulation capacity. 3. Introduce a two-layer control strategy for adaptive regulation capacity allocation and precise online control. | Subsystem | Building thermal, HVAC pipe network | Subsystem | White-Box | Thermodynamic modeling (Equivalent Thermal Parameter model for room), Transfer function-based modeling of CAC systems using components from Modelica Buildings Library and EnergyPlus | Time delays modeled as transport phenomena | No | - | Yes | Validated platform | N/A | MATLAB | Virtual testbed | ElectricChiller CAC model from EnergyPlus simulating a building with 5 rooms | Building thermal | Component | White-Box | Physics-based simulation via EnergyPlus | High-fidelity model, no major simplifying assumptions beyond library defaults. | Yes | Chiller | Yes | Validated platform | N/A | EnergyPlus | - | 1min | Outlet set temperature of the chiller, Room set temperature | Medium, High | Regulation tracking accuracy, Indoor comfort maintenance, Responsiveness to different regulation demands | Impact of uncertainties (e.g., CAC withdrawal, cooling load variation) | No | Simulation only | Yes | Model representation limit | DEMAND RESPONSE; ANCILLARY SERVICES; FREQUENCY REGULATION; ENERGY; OPTIMIZATION; ERROR; LOADS | [Xie, Kang; Ding, Yi; Ye, Chengjin] Zhejiang Univ, Coll Elect Engn, Hangzhou, Peoples R China; [Hui, Hongxun; Song, Yonghua] Univ Macau, State Key Lab Internet Things Smart City, Taipa, Macao, Peoples R China; [Zheng, Wandong] Tianjin Univ, Sch Environm Sci & Engn, Tianjin, Peoples R China; [Ye, Shuiquan] RunPaq Technol Co Ltd, Hangzhou, Peoples R China | Zhejiang University; University of Macau; Tianjin University | Hui, HX; Ding, Y (corresponding author), Zhejiang Univ, 38 Zheda Rd, Hangzhou 310027, Peoples R China. | xiekang@zju.edu.cn; hongxunhui@um.edu.mo; yiding@zju.edu.cn; yhsong@um.edu.mo; yechenjing@zju.edu.cn; wdzheng@tju.edu.cn; yeshuiquan@runpaq.com | 23 | 24 | 315 | [5 empty] | 119035
64 | 64 | Fresnel solar cooling plant for buildings: Optimal operation of an absorption chiller through inverse modelling | Delgado, MG; Ramos, JS; Medina, DC; Amores, TRP; Cerezo-Narváez, A; Dominguez, SA | Guerrero Delgado, MCarmen; Sanchez Ramos, Jose; Castro Medina, Daniel; Palomo Amores, Teresa Rocio; Cerezo-Narvaez, Alberto; Alvarez Dominguez, Servando | NOV | 2022 | http://dx.doi.org/10.1016/j.egyr.2022.02.128 | Solar cooling plant; Absorption chiller; Double effect; Inverse modelling; Renewable energy integration | CO | Energy Reports | Absorption chillers in solar cooling systems are underutilized due to challenges in controlling their operation under variable solar conditions. Existing simplified or detailed models often lack experimental validation or fail to integrate with real-time control. There's a gap in methods that link inverse dynamic modeling with plant-level energy management to improve solar utilization and reduce auxiliary gas dependency. | 1. Develop and validate a simplified, experimentally calibrated inverse model of an absorption chiller. 2. Use this model to support predictive control of the auxiliary gas boiler in a solar cooling plant. 3. Demonstrate how predictive control can improve solar fraction, reduce gas consumption, and cut operational costs in a real building setup. | Subsystem | Chiller | Component | Gray-Box | Three-mode (start-up, steady-state, shutdown) thermal model using simplified 1st-order energy balance equations, Manufacturer-based performance curves used during steady-state operation | Lumped thermal mass assumption, Quasi-steady behavior in Mode 2 (normal operation), UA values and thermal capacities are stable within modes | No | - | Yes | Real data | N/A | N/A | Real building | Pilot solar cooling plant at a university building in Seville, Spain, Double-effect LiBr–H₂O absorption chiller (174 kW), Powered by linear Fresnel solar collector and auxiliary natural gas boiler, PCM storage tank included for buffering solar heat | - | - | - | - | - | - | - | - | - | - | - | Decision support system, Data acquisition system | 10min | Auxiliary gas boiler on/off | Low | COP of absorption chiller, Solar fraction, Energy savings (natural gas reduction), Cost reduction | Baseline scenario with no predictive control | Yes | Full-scale real-world deployment | Yes | Model representation limit | SINGLE; SYSTEMS; PERFORMANCE; TECHNOLOGIES; SIMULATION; COLLECTOR; DRIVEN; OPTIMIZATION; VALIDATION; STORAGE | [Guerrero Delgado, MCarmen; Sanchez Ramos, Jose; Castro Medina, Daniel; Palomo Amores, Teresa Rocio; Alvarez Dominguez, Servando] Univ Seville, Escuela Tecn Super Ingn, Grp Termotecnia, Camino Descubrimientos S-N, Seville 41092, Spain; [Cerezo-Narvaez, Alberto] Univ Cadiz, Dept Ingn Mecan & Diseno Ind, Escuela Super Ingn, Ave Univ Cadiz 10, Cadiz 11519, Spain | University of Sevilla; Universidad de Cadiz | Cerezo-Narváez, A (corresponding author), Univ Cadiz, Dept Ingn Mecan & Diseno Ind, Escuela Super Ingn, Ave Univ Cadiz 10, Cadiz 11519, Spain. | alberto.cerezo@uca.es | 9 | 9 | 8 |  |  |  | 3189 | 3212
65 | 65 | Robust MPC with data-driven demand forecasting for frequency regulation with heat pumps | Bunning, F; Warrington, J; Heer, P; Smith, RS; Lygeros, J | Bunning, Felix; Warrington, Joseph; Heer, Philipp; Smith, Roy S.; Lygeros, John | MAY | 2022 | http://dx.doi.org/10.1016/j.conengprac.2022.105101 | Frequency regulation; Robust Model Predictive Control; Demand forecasting; Electric reserves; District heating; Affine policies | EF | Control Engineering Practice | Traditional frequency regulation approaches in buildings depend heavily on detailed dynamic building models, which are hard to obtain, maintain, and implement in real-world district-scale systems due to infrastructure, privacy, and modeling barriers. | To demonstrate a robust, scalable, and less invasive control strategy for frequency regulation using a three-level control hierarchy that:1. Utilizes Robust Model Predictive Control (MPC) with affine policies. 2. Leverages data-driven ANN-based demand forecasting with online corrections. 3. Uses buffer storage thermal inertia instead of building thermal mass. 4. Validates the approach experimentally on a real-world district-like setup (NEST building, Switzerland). | Subsystem | TES | Component | White-Box | First-principles physics-based models for thermal storage temperature from heat pump and buffer interaction | Thermal losses in storage are negligible. | No | - (prediction model of building heating demand) | Yes | Real data | YALMIP, CPLEX | MATLAB | Real building | NEST building at Empa (Switzerland), a modular “vertical neighborhood” simulating a district. System includes a ground-source heat pump (Viessmann, 50 kW), two 1100 L storage tanks. | - | - | - | - | - | - | - | - | - | - | - | Python OPC-UA client for the communication with sensors and actuators | Level 1 (Reserve planning): Daily; Level 2 (MPC): 15 minutes; Level 3 – PI Tracking: 0.5 sec | Level 1 – Reserve Planning: symmetric frequency regulation reserve; Level 2 – MPC Adjustment: Set points of Electrical power input to the heat pump; Level 3 – PI Tracking: compressor speed | Low, Medium, High | Flexibility: % of electricity available for reserves (13.4% avg), PJM performance score (accuracy, delay, precision), Temperature constraint satisfaction | Open-loop MPC without affine policies | Yes | Full-scale real-world deployment | Yes | Model representation limit | BUILDING COOLING LOAD; NEURAL-NETWORK; SIDE MANAGEMENT; ENERGY DEMAND; PREDICTION; POWER; FLEXIBILITY; SYSTEMS; OPTIMIZATION; OCCUPANCY | [Bunning, Felix; Heer, Philipp] Empa, Urban Energy Syst Lab, Uberlandstr 129, CH-8600 Dubendorf, Switzerland; [Bunning, Felix; Warrington, Joseph; Smith, Roy S.; Lygeros, John] Swiss Fed Inst Technol, Automat Control Lab, Dept Elect Engn & Informat Technol, Zurich, Switzerland | Swiss Federal Institutes of Technology Domain; Swiss Federal Laboratories for Materials Science & Technology (EMPA); Swiss Federal Institutes of Technology Domain; ETH Zurich | Bunning, F (corresponding author), Empa, Urban Energy Syst Lab, Uberlandstr 129, CH-8600 Dubendorf, Switzerland.;Bunning, F (corresponding author), Swiss Fed Inst Technol, Automat Control Lab, Dept Elect Engn & Informat Technol, Zurich, Switzerland. | felix.buenning@empa.ch | 27 | 27 | 122 | [5 empty] | 105101
66 | 66 | H-Infinity Loop-Shaped Model Predictive Control With HVAC Application | Bortoff, SA; Schwerdtner, P; Danielson, C; Di Cairano, S; Burns, DJ | Bortoff, Scott A.; Schwerdtner, Paul; Danielson, Claus; Di Cairano, Stefano; Burns, Daniel J. | SEP | 2022 | http://dx.doi.org/10.1109/TCST.2022.3141937 | Buildings; HVAC; Heat pumps; Standards; Mathematical models; Cost function; Control systems; Cooling; heating; predictive control; robust control | CO | IEEE Transactions on Control Systems Technology | Conventional MPC designs for factory-built HVAC systems suffer from: 1. Poor closed-loop performance due to estimator-controller separation and sensitivity to model uncertainty. 2. A large number of tuning parameters (~1000+), making implementation infeasible for products with limited sensing and control resources. | 1. Propose a Loop-Shaped MPC (LSMPC) based on H∞ loop-shaping that ensures robust stability margin and systematic parameter tuning. 2. Validate the controller in both simulation and experimental lab settings using a multizone air-source heat pump. | Subsystem | ASHP | Subsystem | White-Box | Linearized & reduced from full Modelica-based white-box system | Lumped air volume with ideal mixing | No | - | Yes | Validated platform | N/A | N/A | Lab | MERL's laboratory with a 10kW Mitsubishi multizone heat pump; four indoor test chambers (4.5–9 m³ each), outdoor air chamber, controllable heaters for dynamic loads, LabView integration for control. | - | - | - | - | - | - | - | - | - | - | - | Labview | 30s | Compressor frequency, Outdoor fan speed, Expansion valve openings | Low | Zone temperature tracking, Transient response time (20–30 min rise time), Stability margin | Standard PID controllers, Unconstrained H∞ loop-shaped controller | Partial | Lab setup | Yes | Model representation limit | ROBUST STABILIZATION; CONTROL-SYSTEMS; OPTIMIZATION; CONSUMPTION; TRANSIENT; MPC | [Bortoff, Scott A.; Di Cairano, Stefano; Burns, Daniel J.] Mitsubishi Elect Res Labs, Cambridge, MA 02139 USA; [Schwerdtner, Paul] Tech Univ Berlin, Inst Math, D-10623 Berlin, Germany; [Danielson, Claus] Univ New Mexico, Dept Mech Engn, Albuquerque, NM 87131 USA | Technical University of Berlin; University of New Mexico | Bortoff, SA (corresponding author), Mitsubishi Elect Res Labs, Cambridge, MA 02139 USA. | bortoff@merl.com; schwerdt@.math.tu-berlin.de; cdanielson@unm.edu; dicairano@merl.com; burns@merl.com | 10 | 10 | 30 | 5 |  |  | 2188 | 2203
67 | 67 | Energy Optimization of Air Handling Units Using Constrained Predictive Controllers Based on Dynamic Neural Networks | Asvadi-Kermani, O; Momeni, H; Justo, A; Guerrero, JM; Vasquez, JC; Rodriguez, J; Khan, B | Asvadi-Kermani, Omid; Momeni, Hamidreza; Justo, Andrea; Guerrero, Josep M.; Vasquez, Juan C.; Rodriguez, Jose; Khan, Baseem |  | 2022 | http://dx.doi.org/10.1109/ACCESS.2022.3177660 | Energy consumption; Atmospheric modeling; Adaptation models; Computational modeling; Heating systems; Neural networks; Load modeling; Predictive controller; adaptive control; air handling unit; energy optimization; dynamic neural networks | CO | IEEE Access | Previous studies on HVAC systems using neural networks or MPC often focused on short durations (1–1.5 months), lacked detailed component-level modeling, or did not address control system stability and computational efficiency. Many used static or overly complex models, making real-time implementation challenging. | 1. Develop an energy optimization strategy for AHUs using a hybrid model approach. 2. Model the heat exchanger (H/E) using dynamic recurrent neural networks (RNN) trained on real and simulated data. 3. Implement an adaptive constrained generalized predictive controller (GPC) to reduce computational load while enhancing stability. 4. Control temperature, humidity, and airflow while minimizing energy usage over a full year of operation. | Subsystem | HX | Component | Black-Box | Dynamic recurrent neural network (NARX-type), two-layer linear time-series networks. | Humidity input and output assumed equal for H/E modeling. | Yes | AHU outlet humidity and airflow | Yes | Real data | NARX Toolbox | MATLAB | Virtual testbed | Same NARX-based dynamic neural network model | HX | Component | Black-Box | Dynamic recurrent neural network (NARX-type), two-layer linear time-series networks. | Humidity input and output assumed equal for H/E modeling. | Yes | AHU outlet humidity and airflow | Yes | Real data | Simulink | MATLAB | - | 5min | Inlet water temperature to H/E, Recirculation damper opening and airflow rate | Low, Medium | Energy consumption reduction, Output air temperature tracking error, System stability, Humidity and airflow constraint satisfaction | Previous MPC-based study [3] on same dataset | No | Simulation only | No | The process model and testbed are the same | BUILDINGS; SYSTEMS; MPC | [Asvadi-Kermani, Omid; Momeni, Hamidreza] Tarbiat Modares Univ, Dept Control, Fac Elect & Comp Engn, Tehran 1411713116, Iran; [Justo, Andrea] Univ Autonoma Barcelona, Dept Psychobiol & Methodol Hlth Sci, Bellaterra 08193, Spain; [Guerrero, Josep M.; Vasquez, Juan C.] Aalborg Univ, Ctr Res Microgrids CROM, AAU Energy, DK-9220 Aalborg, Denmark; [Rodriguez, Jose] Univ San Sebastian, Fac Engn, Santiago 8420524, Chile; [Khan, Baseem] Hawassa Univ, Dept Elect & Comp Engn, Hawassa 05, Ethiopia | Tarbiat Modares University; Autonomous University of Barcelona; Aalborg University; Universidad San Sebastian; Hawassa University | Khan, B (corresponding author), Hawassa Univ, Dept Elect & Comp Engn, Hawassa 05, Ethiopia. | baseem.khan04@gmail.com | 4 | 4 | 10 |  |  |  | 56578 | 56590
68 | 68 | Stochastic Optimal Control of HVAC System for Energy-Efficient Buildings | Yang, Y; Hu, GQ; Spanos, CJ | Yang, Yu; Hu, Guoqiang; Spanos, Costas J. | JAN | 2022 | http://dx.doi.org/10.1109/TCST.2021.3057630 | HVAC; Humidity; Fans; Buildings; Uncertainty; Markov processes; Computational modeling; Energy-efficient; heating; ventilation and air-conditioning (HVAC) control; Markov decision process (MDP); predicted mean vote (PMV); stochastic policy | CO | IEEE Transactions on Control Systems Technology | Existing HVAC control strategies struggle with two core issues: (1) managing nonlinear and nonanalytical system dynamics (especially due to complex thermal behavior and the PMV model), and (2) dealing with uncertain thermal disturbances from weather and occupancy. Additionally, most systems still use static temperature bands for comfort, which oversimplifies occupant satisfaction. | 1. Develop an HVAC control strategy that can effectively handle both system nonlinearities and uncertainties. 2. Incorporate a full predicted mean vote (PMV) model for realistic thermal comfort representation. 3. Formulate the control problem as a Markov Decision Process (MDP). 4. Propose a Gradient-Based Learning (GB-L) method to learn stochastic policies offline for real-time execution. | Subsystem | Building thermal, IAQ | Component | Gray-Box | Energy and mass conservation equations for temperature and humidity dynamics | Heat transfer via walls and windows is modeled using linear physics-based relationships. | No | - (PMV) | Yes | Previous Literature | N/A | N/A | Virtual testbed | A simulated office room (6m × 5m × 4m) with 5 occupants. | Building thermal, IAQ | Component | Gray-Box | Energy and mass conservation equations for temperature and humidity dynamics | Heat transfer via walls and windows is modeled using linear physics-based relationships. | No | - | Yes | Previous Literature | N/A | N/A | - | 30min | Supply airflow rates of FAU and FCU, Set-point temperatures of FAU and FCU | Medium | Energy cost, PMV, On-line computation time | Model predictive control–based relaxation (MPC-R) strategy using perfect foresight as a near-optimal bound. | No | Simulation only | No | The process model and testbed are the same | MODEL-PREDICTIVE CONTROL; MANAGEMENT; VENTILATION; SIMULATION | [Yang, Yu] Berkeley Educ Alliance Res Singapore, SinBerBEST, Singapore 138602, Singapore; [Hu, Guoqiang] Nanyang Technol Univ, Sch Elect & Elect Engn, Singapore 639798, Singapore; [Spanos, Costas J.] Univ Calif Berkeley, Dept Elect Engn & Comp Sci, Berkeley, CA 94720 USA | Nanyang Technological University; University of California System; University of California Berkeley | Yang, Y (corresponding author), Berkeley Educ Alliance Res Singapore, SinBerBEST, Singapore 138602, Singapore. | yu.yang@bears-berkeley.sg; gqhu@ntu.edu.sg; spanas@berkeley.edu | 26 | 27 | 30 | 1 |  |  | 376 | 383
69 | 69 | Optimal Strategy for Participation of Commercial HVAC Systems in Frequency Regulation | Liu, H; Xie, HM; Luo, H; Qi, JJ; Goh, HW; Rahman, S | Liu, Hui; Xie, Haimin; Luo, Hui; Qi, Junjian; Goh, Hui Hwang; Rahman, Saifur | 2026-12-01 | 2021 | http://dx.doi.org/10.1109/JIOT.2021.3076434 | HVAC; Fans; Frequency control; Buildings; Regulation; Temperature control; Ducts; Area control error (ACE); frequency regulation; heating; ventilation; and air conditioning (HVAC) system; occupants' comfort; optimal dispatch (OD) | EF | IEEE Internet of Things Journal | Previous studies mostly focus on evaluating HVAC capabilities to track regulation signals or estimating potential regulation capacities. However, they rarely address: 1. Closed-loop dispatch of commercial HVAC systems. 2. Fair consideration of occupant comfort in real-time regulation participation. | 1. Propose a hierarchical framework that enables coordination between power grid and HVAC systems via load aggregators. 2. Develop an optimal closed-loop strategy to allocate real-time frequency regulation tasks to HVAC systems. 3. Ensure fairness in occupant comfort by minimizing deviation from temperature setpoints during regulation. | Subsystem | Building thermal | Component | White-Box | First-order RC model | Lumped zone thermal dynamics with linear resistance-capacitance (RC) formulation. | Yes | Fan | No | None | N/A | MATLAB | Virtual testbed | Simulated two-area interconnected power system with: 1. 300 load aggregators; 2. Each aggregator controls 100 HVAC systems; 3. Each HVAC system contains 4 zones with varied thermal and disturbance parameters | Building thermal | Component | White-Box | RC-based thermal model with randomized parameters for simulation realism | Lumped zone thermal dynamics with linear resistance-capacitance (RC) formulation. | Yes | Fan | No | None | Simulink | MATLAB | - | N/A | Fan power (through VFD), Distribution coefficient of supply air flow rate | Low, Medium | RMS of frequency deviation, RMS of Area Control Error (ACE), Mean Absolute Temperature Deviation (ATD) from setpoints, Energy consumption | Proportional Dispatch (PD), No Dispatch (WD) | No | Simulation only | No | The process model and testbed are the same | ANCILLARY SERVICE; CHILLER CONTROL; HEAT-PUMP; BUILDINGS; MODEL; PERFORMANCE; ALGORITHM | [Liu, Hui; Xie, Haimin; Goh, Hui Hwang] Guangxi Univ, Sch Elect Engn, Nanning 530004, Peoples R China; [Luo, Hui] Guangxi Power Grid, Bur Nanning Power Supply, Nanning 530004, Peoples R China; [Qi, Junjian] Stevens Inst Technol, Dept Elect & Comp Engn, Hoboken, NJ 07030 USA; [Rahman, Saifur] Virginia Tech, Adv Res Inst, Arlington, VA 22203 USA | Guangxi University; China Southern Power Grid; Stevens Institute of Technology; Virginia Polytechnic Institute & State University | Xie, HM (corresponding author), Guangxi Univ, Sch Elect Engn, Nanning 530004, Peoples R China. | hughlh@126.com; xhm2230@163.com; luohui_2019@126.com; jqi8@stevens.edu; hhgoh@gxu.edu.cn; srahman@vt.edu | 18 | 18 | 8 | 23 |  |  | 17100 | 17110
70 | 70 | Model Predictive Control of Smart Districts With Fifth Generation Heating and Cooling Networks | Taylor, M; Long, S; Marjanovic, O; Parisio, A | Taylor, Michael; Long, Sebastian; Marjanovic, Ognjen; Parisio, Alessandra | DEC | 2021 | http://dx.doi.org/10.1109/TEC.2021.3082405 | Water heating; Heat pumps; Substations; Hydraulic systems; Energy management; Electronic countermeasures; Bidirectional control; Model predictive control; smart districts; district heating and cooling; multi-energy systems | CO | IEEE Transactions on Energy Conversion | Lack of generalizable modeling techniques that support integration of 5GDHC networks into MPC for smart district energy management. Existing tools often neglect multi-energy interactions, decentralized pumps, and WSHP dynamics in tractable control formulations. | 1. Extend the COMMES framework to include 5GDHC substations (with WSHPs), hydraulic pumps, and multi-energy networks. 2. Develop an economic MPC (eMPC) formulation for smart districts. 3. Demonstrate improved operational performance via simulation against a rule-based baseline. | Subsystem | TES | Component | White-Box | First-order discrete-time state-space model with parameters drawn from engineering knowledge (e.g., literature, specs). | Linear storage dynamics, constant decay and efficiencies | Yes | Energy Conversion Model (ECM), Network (electricity/gas/thermal), WSHPs, Chillers, μ-CHP, Pumps, Prosumers (loads, PV, etc.) | No | None | CPLEX | MATLAB | Virtual testbed | A simulated smart district with three interconnected hubs (office, supermarket, DHC hub), 5GDHC loop, electrical/gas networks, batteries, WSHPs, μ-CHP, solar PV, and storage. | TES | Component | White-Box | First-order discrete-time state-space model with parameters drawn from engineering knowledge (e.g., literature, specs). | Linear storage dynamics, constant decay and efficiencies | Yes | Energy Conversion Model (ECM), Network (electricity/gas/thermal), WSHPs, Chillers, μ-CHP, Pumps, Prosumers (loads, PV, etc.) | No | None | N/A | MATLAB | - | 30min | Charging/discharging rates of thermal and battery storage, Power import/export from external networks, Operation modes of WSHPs, pumps, μ-CHP, and chiller | Medium | Total operational energy cost, Storage utilization, Adherence to network constraints (e.g., electrical feeder capacity) | Rule-Based Controller (RBC) with tuned price thresholds | No | Simulation only | No | The process model and testbed are the same | OPTIMIZATION; SYSTEMS | [Taylor, Michael; Long, Sebastian; Marjanovic, Ognjen; Parisio, Alessandra] Univ Manchester, Sch Engn, Dept Elect & Elect Engn, Manchester M13 9PL, Lancs, England | University of Manchester | Taylor, M (corresponding author), Univ Manchester, Sch Engn, Dept Elect & Elect Engn, Manchester M13 9PL, Lancs, England. | michael.taylor-6@manchester.ac.uk; long@manchester.ac.uk; Ognjen.Marjanovic@manchester.ac.uk; parisio@manchester.ac.uk | 18 | 19 | 36 | 4 |  |  | 2659 | 2669
71 | 71 | Energy-efficient operation of a complete Chiller-air handing unit system via model predictive control | Wang, WY; Zhou, Q; Pan, C; Cao, F | Wang, Wenyi; Zhou, Qun; Pan, Chao; Cao, Feng | 2026-01-25 | 2022 | http://dx.doi.org/10.1016/j.applthermaleng.2021.117809 | Chiller-air handling units system; Detailed dynamical model; Model predictive control; Energy saving; Cost reduction | CO | Applied Thermal Engineering | Existing control strategies for Chiller-AHU systems often focus on reducing electricity bills through demand response, such as precooling strategies, rather than minimizing total energy consumption. They also tend to model subsystems in isolation or assume a constant chiller COP, neglecting the interactions among components and realistic part-load behavior. | 1. Develop a comprehensive, control-oriented dynamic model of a complete Chiller-AHU system, including AHUs, chilled water loop, and chiller with time-varying COP. 2. Design and implement a nonlinear MPC strategy to minimize total energy consumption and cost while maintaining zone temperature requirements under disturbances. | Whole System | Building thermal, AHU | Subsystem | White-Box | AHU: Physics-based with energy balance equations; Thermal Zone: 2nd-order RC network | 1D flow for water and air in AHUs; Lumped air volume with ideal mixing | Yes | Chiller, Fan/pump power | No | None | N/A | N/A | Virtual testbed | Virtual simulation of one chiller, one water pump, and two AHUs, Zones differ in solar radiation and internal gains | Building thermal, AHU | Subsystem | White-Box | AHU: Physics-based with energy balance equations; Thermal Zone: 2nd-order RC network | 1D flow for water and air in AHUs; Lumped air volume with ideal mixing | Yes | Chiller, Fan/pump power | No | None | N/A | N/A | - | 5min | Supply air temperature, Chilled water supply temperature, Supply air mass flow rate, Chilled water mass flow rate, Outdoor air damper ratio | Medium | Total power consumption (fan + pump + chiller), Electricity cost, Room temperature deviation from setpoint | Traditional PI control with various Tsw and Tsa settings | No | Simulation only | No | The process model and testbed are the same | DEMAND RESPONSE; OPTIMIZATION; IDENTIFICATION; BUILDINGS; FRAMEWORK; NETWORK; SAVINGS; MPC | [Wang, Wenyi; Zhou, Qun] Univ Cent Florida, Dept Elect & Comp Engn, Orlando, FL 32816 USA; [Pan, Chao] Univ Texas Dallas, Dept Mech Engn, Richardson, TX 75080 USA; [Cao, Feng] Xi An Jiao Tong Univ, Sch Energy & Power Engn, 28 Xianning West Rd, Xian 710049, Peoples R China | State University System of Florida; University of Central Florida; University of Texas System; University of Texas Dallas; Xi'an Jiaotong University | Cao, F (corresponding author), Xi An Jiao Tong Univ, Sch Energy & Power Engn, 28 Xianning West Rd, Xian 710049, Peoples R China. | fcao@mail.xjtu.edu.cn | 21 | 22 | 201 |  | B |  |  |  | 117809
72 | 72 | Fault detection and diagnosis for variable-air-volume systems using combined residual, qualitative and quantitative techniques | Wei, D; Feng, HD; Han, Q; Jia, K | Wei, Dong; Feng, Haodong; Han, Qi; Jia, Kun | 2026-01-01 | 2022 | http://dx.doi.org/10.1016/j.enbuild.2021.111491 | Fault detection; Fault diagnosis; Variable-air-volume system; Residuals; Qualitative rules; Quantitative model; Skyspark | FDD | Energy and Buildings | 1. Most FDD strategies focus on local/component-level faults and struggle with progressive faults due to complex system dynamics and subtle symptoms. 2. Lack of system-level fault detection and integration of both model-based and rule-based approaches in real building settings. | 1. Develop a hierarchical FDD framework for VAV systems that combines residual analysis, qualitative rules, and quantitative simulation. 2. Improve accuracy and scalability of fault detection from system-level energy anomalies down to component-level identification. 3. Demonstrate the method using real building data and validate fault detection using a simulation-based fault library. | Subsystem | Building thermal | Component | Black-Box, White-Box | Both black-box and white-box models are developed for building thermal dynamics. Black-box: ANN with Bayesian regularization (time k-1 to k); White-box: TRNSYS-based model | Fault-free operational behavior can be learned from historical data; Physics-based modeling in TRNSYS | No | - | Yes | Real data | N/A | TRNSYS | Historical data | A 22-story public office building in Beijing equipped with a VAV system, ice storage, magnetic chillers, and Skyspark platform. | - | - | - | - | - | - | - | - | - | - | - | - | 15min | - | - | Residual thresholds, Pearson correlation coefficient (>0.85 for fault confirmation) | None | No | Simulation only | Yes | Model representation limit | PREDICTIVE CONTROL; HVAC SYSTEMS; STRATEGY | [Wei, Dong; Feng, Haodong] Beijing Univ Civil Engn & Architecture Search, Beijing, Peoples R China; [Wei, Dong] Beijing Key Lab Intelligent Proc Bldg Big Data, Beijing, Peoples R China; [Han, Qi] Shandong Dawei Int Architectural Design Co Ltd, Jinan, Shandong, Peoples R China; [Jia, Kun] China Elect Engn Design Inst Co Ltd, Beijing, Peoples R China | Beijing University of Civil Engineering and Architecture Search; Beijing Key Laboratory of Intelligent Processing for Building Big Data; Shandong Dawei International Architectural Design Co.Ltd, China Electronics Engineering Design Institute Co.Ltd | Jia, K (corresponding author), China Elect Engn Design Inst Co Ltd, Beijing, Peoples R China. | weidong@bucea.edu.cn; fenghaodong2020@foxmail.com; hanqismx@163.com; jjiakun@ceedi.cn | 9 | 9 | 254 | [5 empty] | 111491
73 | 73 | A nonlinear control approach for hybrid solar thermal plants based on operational conditions | Pataro, IML; Gil, JD; da Costa, MVA; Guzmán, JL; Berenguel, M | Pataro, Igor M. L.; Gil, Juan D.; Americano da Costa, Marcus, V; Guzman, Jose L.; Berenguel, Manuel | JAN | 2022 | http://dx.doi.org/10.1016/j.renene.2021.10.057 | Hybrid control solar thermal plant process; control solar energy model predictive; controller | CO | Renewable Energy | Solar thermal plants involve complex configurations with interacting subsystems (e.g., solar field, tanks, gas heater), and existing control methods either ignore operating mode variations or introduce high computational complexity via external decision-making structures. Prior hybrid controllers did not incorporate varying load demands or used overly complex combinatorial strategies for mode transitions. | To develop a simplified Hybrid Practical Nonlinear Model Predictive Control (HPNMPC) framework that: 1. Integrates operating conditions directly into the control problem, 2. Avoids external decision-makers, 3. Minimizes computation via MIQP formulation, 4. Improves control performance under real disturbances and demand variations. | Subsystem | Solar thermal plant | Subsystem | Gray-Box | Lumped-parameter models for collector and heater, stratified tank models, and steady-state heat exchanger model with first-order dynamic filters for its output temperatures, embedded into a hybrid MLD (Mixed Logical Dynamical) framework. | 1. Simplified dynamic equations (1st order for heat exchange), 2. Piecewise operating modes represented by binary logic, 3. Load demand modeled via temperature ranges, 4. Gas heater regulation fixed at constant value. | No | - | Yes | Real data | Optimization Toolbox, CPLEX | MATLAB | Virtual testbed | The simulation is based on a validated model of the CIESOL solar thermal facility (Spain), including solar collector field, two stratified tanks, a gas heater, and a heat exchanger serving an HVAC system. Tested for "Winter mode" operation. | Solar thermal plant | Subsystem | Gray-Box | Same as process model (MLD-based hybrid modeling). | Same as process model (1st-order models, static mixing, logical switching for subsystems). | No | - | Yes | Real data | N/A | MATLAB | - | 5s | Volumetric flows: u1: pump to tanks; u2: solar collector field; u3: gas heater and exchanger | Low | SAE (Sum of Absolute Error), SCI (Sum of Control Increments), Number of mode changes, Gas heater operation time | Classical PNMPC with external decision-maker | No | Simulation only | No | The process model and testbed are the same | PREDICTIVE CONTROL | [Pataro, Igor M. L.; Gil, Juan D.; Guzman, Jose L.; Berenguel, Manuel] Univ Almeria, Ctr Mixto CIESOL, ceiA3, Ctra Sacramento S-N, Almeria 04120, Spain; [Americano da Costa, Marcus, V] Univ Fed Bahia, Dept Chem Engn, R Prof Aristides Novis 2, Salvador, BA, Brazil | Universidad de Almeria; Universidade Federal da Bahia | Pataro, IML (corresponding author), Univ Almeria, Ctr Mixto CIESOL, ceiA3, Ctra Sacramento S-N, Almeria 04120, Spain. | ilp428@inlumine.ual.es; juandiego.gil@ual.es; marcus.americano@ufba.br; joguzman@ual.es; beren@ual.es | 12 | 12 | 183 |  |  |  | 114 | 129
74 | 74 | Machine-learning-based model predictive control with instantaneous linearization-A case study on an air-conditioning and mechanical ventilation system | Yang, SY; Wan, MP | Yang, Shiyu; Wan, Man Pun | 2026-01-15 | 2022 | http://dx.doi.org/10.1016/j.apenergy.2021.118041 | Model predictive control; Machine learning; Recurrent neural network; Instantaneous linearization; Air conditioning and mechanical ventilation | CO | Applied Energy | The study proposes a novel ML-based MPC scheme incorporating an Instantaneous Linearization (IL) method. This system recurrently linearizes the nonlinear ML model at each control interval using real-time data, enabling linear MPC formulation. The paper experimentally evaluates the control performance of this system in a real hospital office setting and compares it with both a nonlinear ML-based MPC and a traditional thermostat | The study proposes a novel ML-based MPC scheme incorporating an Instantaneous Linearization (IL) method. This system recurrently linearizes the nonlinear ML model at each control interval using real-time data, enabling linear MPC formulation. The paper experimentally evaluates the control performance of this system in a real hospital office setting and compares it with both a nonlinear ML-based MPC and a traditional thermostat | Subsystem | Indoor air temperature, IAQ | Component | Black-Box | NARX Recurrent Neural Network (RNN) with Multi-Layer Perceptron (MLP) architecture | 1. Occupancy load inferred from CO₂ return air concentration 2. Constant air velocity and equipment heat loads 3. No consideration of external weather due to basement location | No | - | Yes | Real data | Deep Learning Toolbox | MATLAB | Real building | A 100 m² office in the basement of a hospital in Singapore. The room is conditioned by a Fan Coil Unit (FCU) system with a 15 kW cooling coil and a Constant Air Volume (CAV) fan supplying 2300 m³/hr. Indoor space considered as a single thermal zone. | - | - | - | - | - | - | - | - | - | - | - | Sensors: Greystone-RH 110B, Titan-TPRS/BB/40, Greystone-ESF-35–2, Greystone-HTDI, Greystone-CDDT, Kamstrup-MULTICAL®602; Advantech ADAM-4019 & 4024 I/O modules | 5min | Cooling power setpoint of the FCU | Medium | Indoor PMV, Energy consumption, CPU processing time | Reactive thermostat (PID control), ML-based MPC without IL | Yes | Full-scale real-world deployment | Yes | Model representation limit | BUILDING ENERGY OPTIMIZATION; THERMAL COMFORT; NEURAL-NETWORK; MANAGEMENT | [Yang, Shiyu] Nanyang Technol Univ, Energy Res Inst NTU ERI N, Singapore 637553, Singapore; [Wan, Man Pun] Nanyang Technol Univ, Sch Mech & Aerosp Engn, Singapore 639798, Singapore | Nanyang Technological University; Nanyang Technological University | Wan, MP (corresponding author), Nanyang Technol Univ, Sch Mech & Aerosp Engn, Singapore 639798, Singapore. | mpwan@ntu.edu.sg | 37 | 38 | 306 |  | B |  |  |  | 118041
75 | 75 | Data-driven district energy management with surrogate models and deep reinforcement learning | Pinto, G; Deltetto, D; Capozzoli, A | Pinto, Giuseppe; Deltetto, Davide; Capozzoli, Alfonso | 2026-12-15 | 2021 | http://dx.doi.org/10.1016/j.apenergy.2021.117642 | Coordinated energy management; Deep reinforcement learning; Long short-term memory neural network; Data-driven modelling; Building energy flexibility | EF | Applied Energy | 1. Existing coordinated district energy management (DEM) often targets schedulable appliances, underutilizing HVAC systems. 2. Many strategies focus on local energy production with pre-computed building demands, ignoring user comfort and indoor temperature control. 3. Model Predictive Control (MPC) faces scalability challenges due to complexity and computational cost, especially for multi-building systems. RL remains underexplored in large-scale DEM. | 1. To develop a fully data-driven, centralized energy management approach using LSTM and Soft Actor-Critic (SAC) DRL. 2. To optimize cost, comfort, and peak load management at the district level. 3. To demonstrate the benefits of controlling HVAC operations and thermal storage across four buildings. | Subsystem | Indoor air temperature | Component | Black-Box | LSTM (Long Short-Term Memory neural networks) | Simplified representation using weather, occupancy, and past temperature/cooling load. | No | - | Yes | Simulated data | PyTorch | Python | Virtual testbed | Four DOE commercial reference buildings: Small Office, Retail, Restaurant, Medium Office. Location: Albuquerque, New Mexico (Climate Zone 4B). | Building thermal | Component | Black-Box | LSTM (Long Short-Term Memory neural networks) | Simplified representation using weather, occupancy, and past temperature/cooling load. | No | - | Yes | Simulated data | N/A | Python | - | 1h | Heat pump cooling power, Chilled water storage charge/discharge, DHW storage charge/discharge | Low | Electricity cost, Peak demand, Peak-to-Average Ratio (PAR), Flexibility factor, Thermal comfort violations | Manually optimized Rule-Based Controller (RBC) with ideal setpoint at 26°C | No | Simulation only | No | The process model (environment) and testbed are the same | DEMAND RESPONSE; PREDICTIVE CONTROL; STORAGE; POWER; TEMPERATURE; BUILDINGS; COMFORT; LOAD; OPTIMIZATION; DESIGN | [Pinto, Giuseppe; Deltetto, Davide; Capozzoli, Alfonso] Politecn Torino, Dept Energy, TEBE Res Grp, BAEDA Lab, Corso Duca Abruzzi 24, I-10129 Turin, Italy | Polytechnic University of Turin | Capozzoli, A (corresponding author), Politecn Torino, Dept Energy, TEBE Res Grp, BAEDA Lab, Corso Duca Abruzzi 24, I-10129 Turin, Italy. | alfonso.capozzoli@polito.it | 80 | 80 | 304 | [5 empty] | 117642
76 | 76 | Model predictive control strategy using encoder-decoder recurrent neural networks for smart control of thermal environment | Li, Y; Tong, ZM | Li, Yue; Tong, Zheming | OCT | 2021 | http://dx.doi.org/10.1016/j.jobe.2021.103017 | Model predictive control; Recurrent neural networks; Thermal environment; Computational fluid dynamics; Smart control | CO | Journal of Building Engineering | 1. Few prior studies combine deep learning (DL) models with Model Predictive Control (MPC) for building thermal environment control. 2. Lack of high-fidelity dynamic co-simulation platforms that integrate CFD with HVAC modeling to realistically assess control strategies. | 1. Develop a DL-based MPC framework using encoder-decoder recurrent neural networks (RNNs) for real-time HVAC control. 2. Implement a co-simulation platform integrating Modelica, CFD, and Python to realistically evaluate control performance. 3. Conduct two case studies (confined space & office with solar radiation) to compare DL-MPC with PID and adaptive PID control strategies. | Subsystem | Indoor air temperature | Component | Black-Box | Encoder-decoder RNN (LSTM and GRU variants) | Building dynamics can be captured by historical indoor/outdoor temperature, HVAC inputs, and environmental data. | No | - | Yes | Simulated data | PyTorch | Python, MATLAB | Virtual testbed | Case 1: 1.04m³ confined chamber with floor heating and mixing ventilation. Case 2: Office room with solar radiation, equipped with inlet/outlet vents and internal heat sources. | CAV system, Indoor temperature and airflow field | Subsystem | White-Box | CFD with RANS k-ε turbulence model + Modelica-based HVAC simulation | Well-characterized geometry and boundary conditions. Radiative heat modeled with S2S (Surface-to-Surface) method. | No | - | Yes | Lab | Simulink, Modelica Buildings Library | MATLAB, Modelica, CFD | - | 10min | Supply air temperature | Medium | Discomfort index, Cooling power | Traditional PID control, Adaptive PID, Physics-based MPC | No | Simulation only | Yes | Model representation limit | BUILDING ENERGY OPTIMIZATION; FAST FLUID-DYNAMICS; OFFICE ENVIRONMENT; INDOOR ENVIRONMENT; COMFORT MANAGEMENT; VENTILATION; OPERATION; SYSTEM; CFD; IMPLEMENTATION | [Li, Yue; Tong, Zheming] Zhejiang Univ, State Key Lab Fluid Power & Mechatron Syst, Hangzhou 310027, Peoples R China; [Li, Yue; Tong, Zheming] Zhejiang Univ, Sch Mech Engn, Hangzhou 310027, Peoples R China | Zhejiang University; Zhejiang University | Tong, ZM (corresponding author), Zhejiang Univ, State Key Lab Fluid Power & Mechatron Syst, Hangzhou 310027, Peoples R China. | tzm@zju.edu.cn | 25 | 27 | 42 | [5 empty] | 103017
77 | 77 | Model predictive control for the operation of a transcritical CO2 air source heat pump water heater | Wang, WY; Zhao, ZF; Zhou, Q; Qiao, YY; Cao, F | Wang, Wenyi; Zhao, Zhongfan; Zhou, Qun; Qiao, Yiyuan; Cao, Feng | 2026-10-15 | 2021 | http://dx.doi.org/10.1016/j.apenergy.2021.117339 | Air source heat pump; transcritical CO2 system; Model predictive control; Optimal heat rejection pressure; Data-driven model | CO | Applied Energy | Existing control strategies for CO₂ ASHP water heaters—especially PID-based ones relying on empirical correlations—are inadequate under realistic, dynamic operating conditions due to slow response, non-optimal performance, and inability to adapt quickly to disturbances such as ambient temperature fluctuation. | 1. Develop a model predictive control (MPC) strategy that directly optimizes the system’s performance without relying on correlation-based reference tracking. 2. Construct a high-fidelity dynamic physical model using Dymola. 3. Derive a data-driven control-oriented model through nonlinear system identification. 4. Demonstrate MPC effectiveness under fixed, realistic, and variable setpoint conditions. | Component | ASHP | Component | Black-Box | Data-driven nonlinear state-space modeling using kernel functions and regularized regression (e.g., L1/L2 norm) | Neglect pressure drops and heat losses in components, Constant compressor frequency (50 Hz), Air/water temperature unaffected by pump/fan | No | - | Yes | Simulated data | N/A | N/A | Virtual testbed | High-fidelity Dymola simulation of a 47 kW CO₂ ASHP water heater with components including tube-in-tube heat exchangers, fan, pump, EEV, and separator. | ASHP | Component | White-Box | Physics-based modeling using thermodynamic modules | Constant compressor speed, Constant water inlet temperature (12°C), No heat losses, Ideal component behavior (isenthalpic throttling, Newtonian heat transfer) | No | - | Yes | Validated platform | TIL Suite | Modelica | - | 3min | Water mass flow rate, EEV (expansion valve) flow area | Low | COP, Heating capacity, Power consumption, Convergence time | PI control with correlation-based setpoints, Sequential Quadratic Programming (SQP)-based optimal conditions | No | Simulation only | Yes | Model representation limit | OPTIMAL DISCHARGE PRESSURE; OPTIMUM HIGH-PRESSURE; NEURAL-NETWORK PART; REJECTION PRESSURE; CARBON-DIOXIDE; OPTIMIZATION; SYSTEMS; CYCLES; GMDH | [Wang, Wenyi; Zhou, Qun; Qiao, Yiyuan] Univ Cent Florida, Dept Elect & Comp Engn, Orlando, FL 32816 USA; [Zhao, Zhongfan] Univ Texas Dallas, Dept Elect Engn, Richardson, TX 75080 USA; [Cao, Feng] Xi An Jiao Tong Univ, Sch Energy & Power Engn, Xian 710049, Peoples R China | State University System of Florida; University of Central Florida; University of Texas System; University of Texas Dallas; Xi'an Jiaotong University | Cao, F (corresponding author), Xi An Jiao Tong Univ, Sch Energy & Power Engn, Xian 710049, Peoples R China. | fcao@mail.xjtu.edu.cn | 40 | 41 | 300 | [5 empty] | 117339
78 | 78 | Data-driven model predictive control for power demand management and fast demand response of commercial buildings using support vector regression | Tang, R; Fan, C; Zeng, FZ; Feng, W | Tang, Rui; Fan, Cheng; Zeng, Fanzhe; Feng, Wei | MAR | 2022 | http://dx.doi.org/10.1007/s12273-021-0811-x | demand response; support vector regression; machine learning; building peak demand; model predictive control; smart grid | EF | Building Simulation | Few existing studies have applied data-driven MPC, especially using support vector regression (SVR), to optimize HVAC operation for fast demand response (DR) in buildings. RC models dominate MPC applications but are time-consuming and inflexible. There is a lack of practical control strategies to immediately reduce power demand while maintaining acceptable indoor environments. | 1. Propose an SVR-based data-driven MPC for fast DR control. 2. Compare performance against traditional RC-based MPC. 3. Investigate three DR scenarios with different objectives (min/smooth power, max/smooth reduction, max average reduction). 4. Improve optimization via GA with constrained search space and temperature-constraint penalties. | Whole System | Indoor air temperature | Component | Black-Box | Support Vector Regression (SVR) with RBF kernel | Indoor temp is mainly driven by chiller power, previous indoor temp, outdoor temp, and time of day | No | - | Yes | Simulated data | N/A | MATLAB | Virtual testbed | TRNSYS simulation of a high-rise commercial building in Hong Kong with 6 chillers, variable speed pumps, and modeled AHUs | HVAC system | Whole System | White-Box | TRNSYS-based HVAC plant simulation using physics-driven models | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | N/A | TRNSYS | - | 15min | Chiller power demand set-point | Medium | Average power reduction, Standard deviation of power demand (smoothness), Maximum indoor temperature | RC-based MPC | No | Simulation only | Yes | Model representation limit | AIR-CONDITIONING SYSTEMS; DIRECT LOAD CONTROL; CONTROL STRATEGY; URGENT REQUESTS; COOLING LOAD; OPTIMIZATION; EFFICIENT; CHALLENGES | [Tang, Rui] UCL, Inst Environm Design & Engn, London, England; [Fan, Cheng] Shenzhen Univ, Minist Educ, Key Lab Resilient Infrastruct Coastal Cities, Shenzhen, Peoples R China; [Fan, Cheng] Shenzhen Univ, Sino Australia Joint Res Ctr BIM & Smart Construc, Shenzhen, Peoples R China; [Zeng, Fanzhe] Shenyang Jianzhu Univ, Sch Municipal & Environm Engn, Shenyang, Peoples R China; [Feng, Wei] Lawrence Berkeley Natl Lab, China Energy Grp, Berkeley, CA USA | University of London; University College London; Shenzhen University; Shenzhen University; Shenyang Jianzhu University; United States Department of Energy (DOE); Lawrence Berkeley National Laboratory | Fan, C (corresponding author), Shenzhen Univ, Minist Educ, Key Lab Resilient Infrastruct Coastal Cities, Shenzhen, Peoples R China.;Fan, C (corresponding author), Shenzhen Univ, Sino Australia Joint Res Ctr BIM & Smart Construc, Shenzhen, Peoples R China. | fancheng@szu.edu.cn | 38 | 39 | 15 | 3 |  |  | 317 | 331
79 | 79 | Simulation and optimal control of heating and cooling systems: A case study of a commercial building | Sampaio, PR; Salvazet, R; Mandel, P; Becker, G; Chenu, D | Sampaio, Phillipe R.; Salvazet, Raphael; Mandel, Pierre; Becker, Gwenaelle; Chenu, Damien | 2026-09-01 | 2021 | http://dx.doi.org/10.1016/j.enbuild.2021.111102 | Optimal control; Grey-box model; Energy efficiency; Black-box optimization; Heating and cooling | CO | Energy and Buildings | Conventional building heating/cooling operations use fixed schedules and conservative rules that ignore day-to-day variations in thermal needs due to weather, occupancy, and other dynamics. Classical MPCs also embed complex DAEs directly in optimization, leading to high computational cost and limited flexibility. | 1. Propose a model-based predictive control (MPC) strategy for heating and cooling optimization using a grey-box model. 2. Develop a black-box optimization framework decoupled from the physical model, reducing computational time. 3. Apply the approach in a real commercial building and evaluate energy savings and model prediction accuracy. | Whole System | Building thermal | Component | Gray-Box | RC network model (R6C2) inspired by Berthou et al., using differential-algebraic equations (DAEs); calibrated using NSGA-II | Steady-state behavior approximated via DAEs with lumped parameters. | No | - | Yes | Real data | N/A | N/A | Real building | A 25,000 m² commercial office building in Brussels (constructed in 2009), with medium thermal inertia, five floors (plus three underground parking), and a typical occupancy from 7 AM to 8 PM. | - | - | - | - | - | - | - | - | - | - | - | BMS | 15min | Day initial time (switch to comfort mode), Night initial time (switch to setback mode), Night set-point indoor temperature (only in heating mode) | High | Energy savings | The building's original (non-optimized) operation with fixed schedules. | Yes | Full-scale real-world deployment | Yes | Model representation limit | MODEL-PREDICTIVE CONTROL; ARTIFICIAL NEURAL-NETWORK; OF-THE-ART; NSGA-II; ENERGY OPTIMIZATION; HVAC SYSTEMS; ALGORITHM; MPC | [Sampaio, Phillipe R.] Chemin Digue BP76, F-78603 Maisons Laffitte, France; [Salvazet, Raphael; Becker, Gwenaelle; Chenu, Damien] 291 Ave Daniel Dreyfous Ducas, F-78520 Limay, France; [Mandel, Pierre] Le Vermont, 28 Blvd Pesaro,TSA 31197, F-92739 Nanterre, France |  | Sampaio, PR (corresponding author), Chemin Digue BP76, F-78603 Maisons Laffitte, France. | sampaio.phillipe@gmail.com; raphael.salva-zet@veolia.com; pierre.mandel@veolia.com; gwenaelle.becker@veolia.com; damien.chenu@veolia.com | 10 | 11 | 246 | [5 empty] | 111102
80 | 80 | Management of a district heating network using model predictive control with and without thermal storage | Quaggiotto, D; Vivian, J; Zarrella, A | Quaggiotto, Davide; Vivian, Jacopo; Zarrella, Angelo | SEP | 2021 | http://dx.doi.org/10.1007/s11081-021-09644-w | Model predictive control; Mixed-integer linear programming; District heating simulation | CO | Optimization and Engineering | Existing district heating networks often lack optimized operational control strategies to enhance economic and environmental performance. Demand Side Management (DSM) in district heating is underutilized due to operators’ limited influence past user substations. | 1. Assess how to optimally operate the heat supply system in a real district heating network using Model Predictive Control (MPC). 2. Compare the cost-effectiveness of leveraging thermal inertia of network pipelines and an added centralized thermal storage tank. 3. Evaluate the impact of these strategies using a detailed simulation of the Verona Centro Città DHN. | Subsystem | DHC, Indoor air temperature | Subsystem | White-Box | Simplify the distributed, nodal, PDE-based model of the district heating network model (Eq. 21) into a lumped, scalar, linear energy balance model (Eq. 2) for use within the MPC optimization. | Network is treated as a single thermal mass with uniform temperature, Heat losses use average of supply and return temperatures, No explicit treatment of node-wise temperature variation | No | - | No | None | N/A | N/A | Virtual testbed | Simulated operation of Verona Centro Città DHN (25 km long, 652 m³ water volume, 70 GWh/year load). | DHC, Indoor air temperature | Subsystem | White-Box | Finite Difference Method (via NeMo tool) | No axial conduction, simplified storage model, fixed supply temp. | No | - | Yes | Real data | N/A | N/A | - | 1h | Heat generation levels (CHP, GB, HP), mass flow rate setpoints | Medium | Operational cost, energy mix shares, return temperature, cost reduction | Basic rule-based control (current operator method), Ideal optimization without MPC feedback | No | Simulation only | Yes | Model representation limit: simplification for control | OPERATIONAL OPTIMIZATION; DISCRETIZATION; SYSTEMS | [Quaggiotto, Davide; Vivian, Jacopo; Zarrella, Angelo] Univ Padua, Dept Ind Engn, Padua, Italy | University of Padua | Quaggiotto, D (corresponding author), Univ Padua, Dept Ind Engn, Padua, Italy. | davide.quaggiotto@phd.unipd.it | 23 | 23 | 22 | 3 |  | SI | 1897 | 1919
81 | 81 | A hierarchical optimal control strategy for continuous demand response of building HVAC systems to provide frequency regulation service to smart power grids | Wang, HL; Wang, SW | Wang, Huilong; Wang, Shengwei | 2026-09-01 | 2021 | http://dx.doi.org/10.1016/j.energy.2021.120741 | Building demand response; Optimal control; HVAC systems; Grid-responsive building; Smart grid | EF | Energy | Existing strategies for HVAC-based frequency regulation do not consider the variability of building energy flexibility over time, particularly for systems like chillers which have a large power draw and strong influence on indoor temperature. Moreover, no previous study has optimized both baseline power use (Pb) and regulation capacity (Creg) while considering HVAC operating constraints and thermal comfort tradeoffs. | 1.Propose a hierarchical optimal control strategy for HVAC systems to provide qualified frequency regulation service. 2. Develop a Maximum Accumulated Offset (MAO) module to handle the stochastic nature of AGC signals and ensure thermal comfort. | Whole System | Building thermal, Chiller | Component | Gray-Box, White-Box | Gray-box state-space model developed from thermal energy balance equations; Chiller modeled using steady-state equations augmented with first-order dynamic transfer functions | Chiller dynamics approximated with first-order lag, Thermal mass lumped as single zone | Yes | Chiller and fan power | Yes | Simulated data | N/A | MATLAB | Virtual testbed | Virtual testbed based on International Commerce Centre (ICC), Hong Kong (490 m high, 321,000 m²). Simulation involves one chiller and one floor of the building. HVAC modeled using TRNSYS components and co-simulated with MATLAB. | HVAC system | Whole System | White-Box | TRNSYS-based HVAC plant simulation using physics-driven models | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Validated platform | N/A | TRNSYS | - | 1h | Indoor temperature setpoint, Chilled water supply temperature setpoint | High, Medium | Composite score for regulation service (correlation, delay, precision), Indoor temperature comfort maintenance, Regulation capacity | Conventional HVAC control (feedback only), Scenarios with and without frequency regulation, under various MAO signal conditions | No | Simulation only | Yes | Model representation limit: Lumped RC model for control | SIMPLIFIED DYNAMIC-MODEL; INTERNAL THERMAL MASS; COMMERCIAL BUILDINGS; DEHUMIDIFYING COILS; ANCILLARY SERVICES; CHILLER CONTROL; PART 1; PERFORMANCE; VALIDATION; RESOURCES | [Wang, Huilong; Wang, Shengwei] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China; [Wang, Huilong] Hong Kong Polytech Univ, Res Inst Sustainable Urban Dev, Kowloon, Hong Kong, Peoples R China | Hong Kong Polytechnic University; Hong Kong Polytechnic University | Wang, SW (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | beswwang@polyu.edu.hk | 42 | 44 | 230 | [5 empty] | 120741
82 | 82 | Peak shaving in district heating exploiting reinforcement learning and agent-based modelling | Solinas, FM; Bottaccioli, L; Guelpa, E; Verda, V; Patti, E | Solinas, Francesco M.; Bottaccioli, Lorenzo; Guelpa, Elisa; Verda, Vittorio; Patti, Edoardo | JUN | 2021 | http://dx.doi.org/10.1016/j.engappai.2021.104235 | Agent-based model; Demand-side management; District heating; Peak shaving; Reinforcement learning | EF | Engineering Applications of Artificial Intelligence | Existing peak shaving strategies for district heating (DH) often neglect the complex thermodynamics of DH networks and the variability in users’ thermal comfort sensitivity. Most literature focuses on electric peak shaving, lacks realistic modeling of DH dynamics, or doesn't integrate user feedback into the control loop. | 1. Flatten the morning thermal demand peak in DH networks without compromising user comfort. 2. Integrate a thermodynamic DH network model, an agent-based model of user comfort, and a reinforcement learning (RL) control agent into a unified decision-making framework. | Subsystem | DHC | Subsystem | Gray-Box | Thermodynamic pipe network model, RC-type building model with an energy balance | Buildings modeled as single-zone equivalents with average indoor temperature, Thermal losses and delays are modeled but thermal diffusion is neglected | No | - (PMV) | Yes | Real data | N/A | N/A | Virtual testbed | Simulated DH network of 66 buildings in Torino using a validated thermodynamic model | DHC | Subsystem | Gray-Box | Thermodynamic pipe network model, RC-type building model with an energy balance | Buildings modeled as single-zone equivalents with average indoor temperature, Thermal losses and delays are modeled but thermal diffusion is neglected | No | - (PMV) | Yes | Real data | N/A | N/A | - | 5min | Heating startup times | High | Peak load reduction, User thermal comfort (PMV, temperature deviation, discomfort penalty), Convergence speed | Genetic Algorithm (GA) optimized control strategy from prior work (Guelpa and Verda 2016) | No | Simulation only | No | The process model (environment) and testbed are the same | NETWORKS; SYSTEMS; OPTIMIZATION; STORAGE | [Solinas, Francesco M.; Bottaccioli, Lorenzo; Patti, Edoardo] Politecn Torino, Dept Control & Comp Engn, I-10129 Turin, Italy; [Bottaccioli, Lorenzo; Guelpa, Elisa; Verda, Vittorio; Patti, Edoardo] Politecn Torino, Energy Ctr Lab, I-10129 Turin, Italy; [Guelpa, Elisa; Verda, Vittorio] Politecn Torino, Dept Energy, I-10129 Turin, Italy | Polytechnic University of Turin; Polytechnic University of Turin; Polytechnic University of Turin | Bottaccioli, L (corresponding author), Politecn Torino, Dept Control & Comp Engn, I-10129 Turin, Italy. | lorenzo.bottaccioli@polito.it | 14 | 14 | 102 | [5 empty] | 104235
83 | 83 | Fault detection and diagnosis for multiple faults of VAV terminals using self-adaptive model and layered random forest | Wang, HT; Feng, DG; Liu, K | Wang, Haitao; Feng, Daoguang; Liu, Kai | 2026-04-15 | 2021 | http://dx.doi.org/10.1016/j.buildenv.2021.107667 | Fault detection and diagnosis; VAV terminal; Multiple faults; Self-adaptive model; Random forest | FDD | Building and Environment | Most existing FDD studies for VAV (Variable Air Volume) terminals struggle with detecting simultaneous multiple faults due to limited data and the complexity of fault interactions. Additionally, many traditional approaches rely on static or poorly adaptive models that cannot maintain predictive accuracy over time. | 1. Develop a self-adaptive zone air-temperature model for accurate fault detection using operational data. 2. Propose a two-layered hybrid fault diagnosis strategy combining rule-based methods and a multi-label random forest approach. 3. Validate the proposed method using real operating data involving 13 single faults and 6 simultaneous-fault cases. | Subsystem | Indoor air temperature | Component | Gray-Box | Thermodynamic heat balance model with self-adaptive parameters, periodically updated via Chaos Particle Swarm Optimization (CPSO) | Air in the zone is well-mixed, Linear heat balance, Constant air properties | No | - | Yes | Real data | N/A | N/A | Historical data | Real data collected from a 36-story commercial office building, involving VAV systems monitored via Building Management System (BMS). Fault cases include 13 single faults and 6 multiple simultaneous faults. | - | - | - | - | - | - | - | - | - | - | - | - | 5min | - | - | Accuracy (ACC), Recall (REC), F1-score, Fault classification success across fault types | None | No | Historical data | Yes | Model representation limit | PARTICLE SWARM OPTIMIZATION; AIR-CONDITIONING SYSTEMS; FDD STRATEGY; SENSOR; CLASSIFICATION; TEMPERATURE; ALGORITHM; NETWORK; PCA | [Wang, Haitao; Feng, Daoguang; Liu, Kai] Henan Univ Technol, Coll Civil Engn, Zhengzhou 450001, Peoples R China | Henan University of Technology | Wang, HT (corresponding author), Henan Univ Technol, Coll Civil Engn, Zhengzhou 450001, Peoples R China. | haitao-wangshd@163.com | 32 | 32 | 193 | [5 empty] | 107667
84 | 84 | Performance improvement of an air-to-water heat pump through linear time-varying MPC with adaptive COP predictor | Rastegarpour, S; Scattolini, R; Ferrarini, L | Rastegarpour, Soroush; Scattolini, Riccardo; Ferrarini, Luca | MAR | 2021 | http://dx.doi.org/10.1016/j.jprocont.2021.01.006 | Air-to-water heat pump; Radiant-floor heating; Linear time-varying control; Predictive control | CO | Journal of Process Control | Most MPC-based heat pump control strategies either assume a constant COP or ignore its dependence on dynamic system variables (e.g., return water temperature). This leads to suboptimal energy use and control performance. | 1. Propose a linear time-varying MPC (MPCLTV) that uses an adaptive COP predictor. 2. Develop two simplified linear COP models and compare them with static and manufacturer-derived approaches. 3. Demonstrate that adaptive modeling improves both prediction and control, with reduced energy consumption and higher COP. | Subsystem | Building thermal, ASHP, TES | Subsystem | Gray-Box | Linearized state-space model derived from the nonlinear model | Linear COP dependence on outdoor and return water temperature. First-order dynamic system for COP evolution. Constant water flow rates in certain subsystems. Single-zone thermal model for building. | No | - | No | None | N/A | N/A | Virtual testbed | A 150 m² radiant-floor building model, 200 L HWT, and modulating air-to-water heat pump validated using experimental data from SYSLAB, Denmark Technical University. | Building thermal, ASHP, TES | Subsystem | Gray-Box | Nonlinear coupled ODE model | First-order dynamic system for COP evolution. Constant water flow rates in certain subsystems. Single-zone thermal model for building. | No | - | Yes | Lab | N/A | N/A | - | 30s | Compressor electrical power , Hot water tank flow rate | Medium | Energy consumption, COP improvement, Indoor temperature | Constant-COP MPC (OCP_const), Manufacturer heating curve (RHC) | No | Simulation only | Yes | Model representation limit: linearization for control | CONTROL-SYSTEMS; HVAC SYSTEMS; ENERGY; MODEL; MANAGEMENT; OPTIMIZATION; COMFORT | [Rastegarpour, Soroush; Scattolini, Riccardo; Ferrarini, Luca] Politecn Milan, Dipartimento Elettron Informaz & Bioingn, Piazza L da Vinci 32, Milan, Italy | Polytechnic University of Milan | Ferrarini, L (corresponding author), Politecn Milan, Dipartimento Elettron Informaz & Bioingn, Piazza L da Vinci 32, Milan, Italy. | Soroush.Rastegarpour@polimi.it; riccardo.scattolini@polimi.it; Luca.Ferrarini@polimi.it | 21 | 22 | 99 |  |  |  | 69 | 78
85 | 85 | Multi-Agent Deep Reinforcement Learning for HVAC Control in Commercial Buildings | Yu, L; Sun, Y; Xu, ZB; Shen, C; Yue, D; Jiang, T; Guan, XH | Yu, Liang; Sun, Yi; Xu, Zhanbo; Shen, Chao; Yue, Dong; Jiang, Tao; Guan, Xiaohong | JAN | 2021 | http://dx.doi.org/10.1109/TSG.2020.3011739 | Buildings; Air quality; Atmospheric modeling; Temperature; Heuristic algorithms; Machine learning; Fans; Commercial buildings; HVAC systems; energy cost; multi-zone coordination; random occupancy; thermal comfort; indoor air quality comfort; multi-agent deep reinforcement learning | CO | IEEE Transactions on Smart Grid | Existing model-based HVAC control strategies (e.g., MPC, convex optimization) require knowledge of thermal dynamics and uncertain parameters, and do not scale well for large discrete decision spaces in multi-zone buildings. Model-free methods (e.g., DQN, DDPG) face instability or neglect spatial coupling and CO₂ control. | To develop a scalable, model-free control algorithm using Multi-Agent Deep Reinforcement Learning (MADRL) with attention mechanisms that: 1. Minimizes HVAC energy cost in multi-zone commercial buildings. 2. Considers random occupancy, thermal comfort, and indoor air quality. 3. Requires no prior knowledge of system dynamics or uncertain parameters. | Subsystem | Indoor air temperature, IAQ | Component | White-Box | Simplified RC model, Mass balance CO2 | Lumped air volume with ideal mixing | Yes | Energy use model | No | None | N/A | Python | Virtual testbed | Simulated commercial building HVAC system with 4–30 thermal zones. | Indoor air temperature, IAQ | Component | White-Box | Simplified RC model, Mass balance CO2 | Lumped air volume with ideal mixing | Yes | Energy use model | No | None | N/A | Python | - | 15min | Zone air supply rate, AHU damper position | Medium, Low | Total energy cost (TEC), Average Temperature Deviation (ATD), Average CO₂ Deviation | Rule-based strategy (RS) based on ON/OFF rules, Heuristic strategy | No | Simulation only | No | The process model (environment) and testbed are the same | DEMAND RESPONSE; ENERGY; SYSTEMS; SMART; MODEL; OPTIMIZATION; PRICE | [Yu, Liang] Nanjing Univ Posts & Telecommun, Coll Automat, Nanjing 210003, Peoples R China; [Yu, Liang; Yue, Dong] Nanjing Univ Posts & Telecommun, Coll Artificial Intelligence, Nanjing 210003, Peoples R China; [Yu, Liang; Xu, Zhanbo; Shen, Chao; Guan, Xiaohong] Xi An Jiao Tong Univ, Key Lab Intelligent Networks & Network Secur, Minist Educ, Xian 710049, Peoples R China; [Sun, Yi] Nanjing Univ Posts & Telecommun, Coll Internet Things, Nanjing 210003, Peoples R China; [Yue, Dong] Nanjing Univ Posts & Telecommun, Coll Automat, Inst Adv Technol, Nanjing 210003, Peoples R China; [Jiang, Tao] Huazhong Univ Sci & Technol, Sch Elect Informat & Commun, Wuhan Natl Lab Optoelect, Wuhan 430074, Peoples R China | Nanjing University of Posts & Telecommunications; Nanjing University of Posts & Telecommunications; Xi'an Jiaotong University; Nanjing University of Posts & Telecommunications; Nanjing University of Posts & Telecommunications; Huazhong University of Science & Technology | Yue, D (corresponding author), Nanjing Univ Posts & Telecommun, Coll Artificial Intelligence, Nanjing 210003, Peoples R China.;Yue, D (corresponding author), Nanjing Univ Posts & Telecommun, Coll Automat, Inst Adv Technol, Nanjing 210003, Peoples R China.;Jiang, T (corresponding author), Huazhong Univ Sci & Technol, Sch Elect Informat & Commun, Wuhan Natl Lab Optoelect, Wuhan 430074, Peoples R China. | medongy@vip.163.com; tao.jiang@ieee.org | 216 | 235 | 12 | 1 |  |  | 407 | 419
86 | 86 | Analysis of Building Parameter Uncertainty in District Heating for Optimal Control of Network Flexibility | Vandermeulen, A; De Jaeger, I; Van Oevelen, T; Saelens, D; Helsen, L | Vandermeulen, Annelies; De Jaeger, Ina; Van Oevelen, Tijs; Saelens, Dirk; Helsen, Lieve | DEC | 2020 | http://dx.doi.org/10.3390/en13236220 | district heating; optimal control; heat demand flexibility; building parameter uncertainty; robust control | CO | Energies | Existing optimal control approaches for district heating systems assume perfect system knowledge and predictions, which is unrealistic due to uncertainties in building parameters affecting heat demand estimation. There's a lack of studies on how these uncertainties impact control performance, especially for network flexibility. | 1. Assess how imperfect knowledge of building parameters (i.e., heat demand magnitude uncertainty) affects the optimal activation and performance of district heating network flexibility. 2. Investigate the sensitivity of control performance to uncertainty in building parameters. 3. Explore strategies for more robust network flexibility control. | Subsystem | District pipe network | Component | White-Box | First-order upwind finite volume method | N/A | Yes | Substation model, Heat pump model, Base and peak plant model | Yes | Simulated data | modesto | N/A | Virtual testbed | Fictive DH network “GenkNET” representing 7775 buildings in Genk, Belgium, aggregated to 9 neighborhoods. Buildings modeled using archetypes with stochastic variations in U-values and other envelope parameters. | DHC | Subsystem | White-Box | TEASER RC-model (4th order) used for optimal building-level heating demand calculation. IDEAS Modelica library used for generating heat demand profiles under uncertainty (500 variants per archetype). | Perfect weather and behavior prediction; only building envelope uncertainty varied. | Yes | Substation, Ideal radiator models | Yes | Validated platform | IDEAS | Modelica | - | 5min | Supply temperature at central plant, Heat generation level (from base, peak unit, or heat pump) | Medium | Cost minimization (heat pump electricity cost; base/peak generation cost), Avoided peak load (for peak shaving), Network flexibility utilization | Baseline scenario with fixed supply temperature, | No | Simulation only | Yes | The process model (used in optimization) assumes deterministic dynamics and perfect system knowledge, whereas the testbed introduces stochastic building parameter uncertainty. | DEMAND RESPONSE; ENERGY SYSTEM; OPTIMIZATION; PREDICTION; IMPLEMENTATION; TRANSPORT; STORAGE; MODEL; TIME | [Vandermeulen, Annelies; De Jaeger, Ina; Van Oevelen, Tijs; Saelens, Dirk; Helsen, Lieve] EnergyVille, Thor Pk 8310, B-3600 Genk, Belgium; [Vandermeulen, Annelies; Helsen, Lieve] Katholieke Univ Leuven, Dept Mech Engn, Celestijnenlaan 300,POB 2421, B-3001 Leuven, Belgium; [Vandermeulen, Annelies; De Jaeger, Ina; Van Oevelen, Tijs] Flemish Inst Technol Res VITO, Boeretang 200, B-2400 Mol, Belgium; [De Jaeger, Ina; Saelens, Dirk] Katholieke Univ Leuven, Dept Civil Engn, Bldg Phys Sect, Kasteelpk Arenberg 40,POB 2447, B-3001 Leuven, Belgium | KU Leuven; VITO; KU Leuven | De Jaeger, I (corresponding author), EnergyVille, Thor Pk 8310, B-3600 Genk, Belgium.;De Jaeger, I (corresponding author), Flemish Inst Technol Res VITO, Boeretang 200, B-2400 Mol, Belgium.;De Jaeger, I (corresponding author), Katholieke Univ Leuven, Dept Civil Engn, Bldg Phys Sect, Kasteelpk Arenberg 40,POB 2447, B-3001 Leuven, Belgium. | annelies.vandermeulen@kuleuven.be; ina.dejaeger@kuleuven.be; tijs.vanoevelen@vito.be; dirk.saelens@kuleuven.be; lieve.helsen@kuleuven.be | 7 | 7 | 13 | 23 |  |  |  |  | 6220
87 | 87 | A Supervised-Learning-Based Strategy for Optimal Demand Response of an HVAC System in a Multi-Zone Office Building | Kim, YJ | Kim, Young-Jin | SEPT | 2020 | http://dx.doi.org/10.1109/TSG.2020.2986539 | Artificial neural networks (ANNs); demand response (DR); heating; ventilating; air-conditioning (HVAC); multi-zone building; supervised-learning-aided meta-prediction | EF | IEEE Transactions on Smart Grid | The paper addresses the challenge of optimizing demand response (DR) in multi-zone buildings, which traditionally requires complex, nonlinear, physics-based HVAC models that are difficult to apply in real buildings due to high modeling and parameter-estimation burdens. | 1. Develop a supervised learning-based strategy that integrates ANN modeling into the DR scheduling framework. 2. Formulate an MILP-compatible ANN representation to ensure global optimization. 3. Propose the SLAMP (Supervised-Learning-Aided Meta-Prediction) method for direct DR scheduling. 4. Validate the approach against traditional physics-based and heuristic ML methods through simulation studies. | Whole System | Indoor air temperature | Component | Black-Box | Deep Nonlinear Auto-Regressive Network with Exogenous Inputs (D-NARX) | Zone temperature dynamics are influenced by power input and thermal conditions (ambient temp, solar radiation, etc.). Each zone modeled independently with coupling implicitly learned from data. | No | - | Yes | Simulated data | N/A | N/A | Virtual testbed | DOE benchmark model of a 6-zone small office building with varying occupancy and solar exposure. | Building thermal | Component | White-Box | Physics-based thermal model with heat transfer and internal gains | Based on DOE reference | Yes | HVAC system | Yes | Validated platform | N/A | EnergyPlus | - | 1h | HVAC system power input | Low | Energy cost, Temperature violation penalty, Computation time | Non-DR baseline (constant power maintaining comfort), Fully-informed physics-based strategy, Other ML-based strategies: PSO-based ANN, DQN-based DR | No | Simulation only | Yes | Model representation limit | ARTIFICIAL NEURAL-NETWORK; AIR-CONDITIONING SYSTEMS; ENERGY-STORAGE; COMMERCIAL BUILDINGS; PREDICTIVE CONTROL; OPTIMIZATION; MODEL; VENTILATION; LEVEL | [Kim, Young-Jin] Pohang Univ Sci & Technol, Dept Elect Engn, Pohang 37673, South Korea | Pohang University of Science & Technology (POSTECH) | Kim, YJ (corresponding author), Pohang Univ Sci & Technol, Dept Elect Engn, Pohang 37673, South Korea. | powersys@postech.ac.kr | 56 | 61 | 11 | 5 |  |  | 4212 | 4226
88 | 88 | Model predictive control with adaptive machine-learning-based model for building energy efficiency and comfort optimization | Yang, SY; Wan, MP; Chen, WY; Ng, BF; Dubey, S | Yang, Shiyu; Wan, Man Pun; Chen, Wanyu; Ng, Bing Feng; Dubey, Swapnil | 2026-08-01 | 2020 | http://dx.doi.org/10.1016/j.apenergy.2020.115147 | Model Predictive Control (MPC); Machine-learning (ML); Artificial Neural Network (ANN); Air Conditioning and Mechanical Ventilation (ACMV); Building Automation and Control (BAC) | CO | Applied Energy | Most ML-based MPC studies are either simulation-based or tested over short durations, and they typically lack mechanisms for continuous model updating. There is also a lack of real-world validation of ML-based models for building control over extended periods. | To develop and experimentally validate a model predictive control (MPC) system that uses an adaptive machine-learning-based dynamic building model. The system aims to optimize energy efficiency and thermal comfort using real-time building data, with continuous model updates via a NARX neural network. | Subsystem | Indoor air temperature, IAQ | Component | Black-Box | Nonlinear Autoregressive Exogenous Neural Network (NARX-ANN) | Office: Assumes well-mixed air and no influence from outdoor temperature due to surrounding air-conditioned spaces. LT: Assumes fixed metabolic rate and clothing insulation for occupants; solar radiation is an unmeasured disturbance. | Yes | Energy use model, (PMV) | Yes | Real data | Optimization Toolbox, Deep Learning Toolbox | MATLAB | Real building | Office: 46 m² room with VAV system in NTU, Singapore. Thermostat-based control replaced by MPC. Lecture Theatre (LT): 255 m² lecture theatre with VAV-AHU and 240 seats; includes sensors for indoor/outdoor conditions and CO₂-based occupancy estimation. | - | - | - | - | - | - | - | - | - | - | - | Sensors: REGIN-HTDT10-420, SIEMENS-QVM62.1, Delta OHM-HP3217.2R, Delta OHM-TP3276.2, Delta OHM-AP3203.2; I/O device; Delta OHM-HD32.3, | 5min | Cooling power setpoint | Medium | PMV index, Room temperature, Energy consumption | Office: Original thermostat-based reactive control; LT: Original Building Management System (BMS) control | Yes | Full-scale real-world deployment | Yes | Model representation limit | ARTIFICIAL NEURAL-NETWORK; THERMAL COMFORT; OCCUPANCY-PREDICTION; GENETIC ALGORITHM; NONLINEAR MPC; HVAC SYSTEMS; IMPLEMENTATION; CONSUMPTION; STRATEGY; CLIMATE | [Yang, Shiyu; Wan, Man Pun; Chen, Wanyu; Ng, Bing Feng] Nanyang Technol Univ, Sch Mech & Aerosp Engn, Singapore 639798, Singapore; [Yang, Shiyu; Dubey, Swapnil] Nanyang Technol Univ, Energy Res Inst NTU ERI N, Singapore 637553, Singapore | Nanyang Technological University; Nanyang Technological University | Wan, MP (corresponding author), Nanyang Technol Univ, Sch Mech & Aerosp Engn, Singapore 639798, Singapore. | mpwan@ntu.edu.sg | 222 | 228 | 271 | [5 empty] | 115147
89 | 89 | Local vs. integrated control of a variable refrigerant flow system using artificial neural networks | Ahn, K; Kim, KJ; Song, K; Park, CS | Ahn, Kiuhn; Kim, Kyung Jae; Song, Kwanwoo; Park, Cheol Soo | 2026-09-13 | 2020 | http://dx.doi.org/10.1080/23744731.2020.1760636 |  | CO | Science and Technology for the Built Environment | Previous studies treated Variable Refrigerant Flow (VRF) systems as local control problems, optimizing control actions based only on local measurements without accounting for the dynamic interactions between the HVAC system and the thermal environment of the served spaces. This limits performance optimization from a whole-system perspective. | The study aims to develop and validate an integrated control strategy for a VRF system that dynamically responds to indoor environmental conditions by leveraging predictive models built using artificial neural networks (ANNs). The goal is to improve energy efficiency and thermal comfort compared to local control strategies. | Subsystem | VRF system | Subsystem | Black-Box | ANN | ANN predictions rely on past 10-minute input sequences (autoregressive) | No | - | Yes | Lab | N/A | MATLAB | Lab | Experimental chamber with: One outdoor unit (23.0 kW cooling capacity), Four indoor units (5.9 kW ×2, 5.1 kW ×2), Outdoor zone simulating weather, and indoor zone of 521.64 m³ | - | - | - | - | - | - | - | - | - | - | - | N/A | 10min | Indoor air set-point temperature, Supply air flow rate of indoor units | High, Medium | Energy use, Indoor temperature | Fixed set-point (26 °C) and mid-level airflow | Partial | Lab setup | Yes | Model representation limit | AIR-CONDITIONING SYSTEM; ENERGY-CONSUMPTION; HVAC SYSTEMS; EVAPORATING TEMPERATURE; RESIDENTIAL SECTOR; CONTROL STRATEGIES; FAULT-DIAGNOSIS; LOAD PREDICTION; VRF SYSTEM; BUILDINGS | [Ahn, Kiuhn] Seoul Natl Univ, Inst Engn Res, 1 Gwanak Ro, Seoul 08826, South Korea; [Kim, Kyung Jae; Song, Kwanwoo] Samsung Elect, SW Dev Grp, Digital Appliance Business, 129 Samsung Ro, Suwon 16677, South Korea; [Park, Cheol Soo] Seoul Natl Univ, Coll Engn, Inst Construct & Environm Engn, Inst Engn Res,Dept Architecture & Architectural E, 1 Gwanak Ro, Seoul 08826, South Korea | Seoul National University (SNU); Samsung Electronics; Samsung; Seoul National University (SNU) | Park, CS (corresponding author), Seoul Natl Univ, Coll Engn, Inst Construct & Environm Engn, Inst Engn Res,Dept Architecture & Architectural E, 1 Gwanak Ro, Seoul 08826, South Korea. | cheolsoo.park@snu.ac.kr | 10 | 11 | 26 | 8 |  |  | 1117 | 1131
90 | 90 | Multi-objective non-simultaneous dynamic optimal control for an ejector expansion heat pump with thermal storages | Liu, F; Qiu, WY; Deng, JX; Mo, Q; Groll, EA; Zhao, J; Liang, JC | Liu, Fang; Qiu, Wenyu; Deng, Jiaxin; Mo, Qiu; Groll, Eckhard A.; Zhao, Jun; Liang, Juncui | 2026-03-05 | 2020 | http://dx.doi.org/10.1016/j.applthermaleng.2019.114835 | Hot and cold thermal storages; Ejector expansion heat pump; Multi-objective dynamic optimal control; Non-simultaneous optimization; Charging performance enhancement | CO | Applied Thermal Engineering | Existing studies on transcritical CO₂ heat pumps with thermal storage largely use conventional expansion valves (ExV) and focus on energy/cost optimization. There is a lack of research on using controllable ejectors and optimizing multiple transient performance objectives dynamically. | 1. Develop a validated dynamic model of a CO₂ ejector expansion heat pump with hot and cold thermal storage (HPTES). 2. Design and evaluate single-objective (SO) and non-simultaneous multi-objective (MO) dynamic optimization strategies. 3. Quantify improvements in COP, energy consumption, and charging time across strategies. | Subsystem | TES coupled HP | Subsystem | White-Box | First-principles modeling using conservation of mass, energy, and momentum | Constant Cp and density of water, 1D transient flow models, Stratified tank discretization, Static ejector geometry during each control stage | No | - | Yes | Lab | TIL Library | Modelica | Virtual testbed | Same Modelica model | TES coupled HP | Subsystem | White-Box | First-principles modeling using conservation of mass, energy, and momentum | Constant Cp and density of water, 1D transient flow models, Stratified tank discretization, Static ejector geometry during each control stage | No | - | Yes | Lab | TIL Library | Modelica | - | N/A | Compressor frequency, Ejector throat area, Hot water flow rate, Cold water flow rate | Low | Transient/overall COP, Energy consumption, Charging time, Heating/cooling capacity |  | No | Simulation only | No | The process model and testbed are the same | ENERGY STORAGE; WATER-HEATER; PERFORMANCE; OPTIMIZATION; SYSTEM | [Liu, Fang; Qiu, Wenyu; Deng, Jiaxin; Mo, Qiu; Liang, Juncui] Shanghai Univ Elect Power, Coll Energy & Mech Engn, 2103 Pingliang Rd, Shanghai 200090, Peoples R China; [Groll, Eckhard A.] Purdue Univ, Sch Mech Engn, Ray W Herrick Labs, 177 S Russel St, W Lafayette, IN 47907 USA; [Liu, Fang; Zhao, Jun] Tianjin Univ, Key Lab Efficient Utilizat Low & Medium Grade Ene, MOE, Tianjin 300350, Peoples R China | Shanghai University of Electric Power; Purdue University System; Purdue University; Purdue University in Indianapolis; Tianjin University | Liu, F (corresponding author), Shanghai Univ Elect Power, Coll Energy & Mech Engn, 2103 Pingliang Rd, Shanghai 200090, Peoples R China. | fangliu@shiep.edu.cn | 18 | 18 | 168 | [5 empty] | 114835
91 | 91 | IoT Based Architecture for Model Predictive Control of HVAC Systems in Smart Buildings | Carli, R; Cavone, G; Ben Othman, S; Dotoli, M | Carli, Raffaele; Cavone, Graziana; Ben Othman, Sarah; Dotoli, Mariagrazia | FEB | 2020 | http://dx.doi.org/10.3390/s20030781 | Internet of Things; Model Predictive Control; Heating Ventilation and Air Conditioning System; Predicted Mean Vote; smart buildings | CO | Sensors | Prior works on MPC for HVAC focus on simulation or algorithm-only implementation and often use simplified comfort indicators (like temperature only). These neglect realistic control architectures, implementation in real environments, and accurate comfort indices like PMV. | 1. Develop a tractable MPC algorithm using a linearized PMV index for thermal comfort. 2. Design and implement a real IoT-based control architecture enabling real-time MPC in smart buildings. 3. Validate the proposed approach through real-world deployment in a university campus lab and compare it with standard thermostat control in terms of energy savings and comfort. | Subsystem | Indoor air temperature | Component | Gray-Box | First-order linear RC model for temperature | Lumped air volume with ideal mixing | No | - (PMV) | Yes | Lab | N/A | MATLAB | Lab | A 36 m² lab at Polytechnic of Bari with 3 controllable fan coil units. | - | - | - | - | - | - | - | - | - | - | - | Multi-protocol gateway Beeta Box, IP device, Message Queuing Telemetry Transport (MQTT), ZigBee, Modbus | 2min | Fan coil unit speed | Low | Energy consumption, Comfort satisfaction rate | Traditional thermostat-based control (with temperature setpoint = 22°C) | Partial | Lab setup | Yes | Model representation limit | TEMPERATURE CONTROL; ENERGY MANAGEMENT; OPTIMIZATION; FRAMEWORK; INTERNET; THINGS | [Carli, Raffaele; Cavone, Graziana; Dotoli, Mariagrazia] Polytech Bari, Dept Elect & Informat Engn, Via Orabona 4, I-70125 Bari, Italy; [Ben Othman, Sarah] Ecole Cent Lille, CRIStAL Lab, UMR 9189, F-59655 Villeneuve Dascq, France | Politecnico di Bari; Universite de Lille; Centrale Lille; Centre National de la Recherche Scientifique (CNRS); CNRS - Institute for Information Sciences & Technologies (INS2I) | Carli, R (corresponding author), Polytech Bari, Dept Elect & Informat Engn, Via Orabona 4, I-70125 Bari, Italy. | raffaele.carli@poliba.it; graziana.cavone@poliba.it; sara.ben-othman@centralelille.fr; mariagrazia.dotoli@poliba.it | 95 | 98 | 20 | 3 |  |  |  |  | 781
92 | 92 | Towards optimal control of air handling units using deep reinforcement learning and recurrent neural network | Zou, ZB; Yu, XR; Ergan, S | Zou, Zhengbo; Yu, Xinran; Ergan, Semiha | FEB | 2020 | http://dx.doi.org/10.1016/j.buildenv.2019.106535 | HVAC control; Energy consumption; Thermal comfort; Deep reinforcement learning; Long-short-term-memory network | CO | Building and Environment | Most existing DRL-based HVAC control strategies rely on simulation environments (e.g., EnergyPlus), which lack accuracy due to incomplete building and HVAC system information. These simulations often neglect many controllable actions like fan speed and damper position and are limited in capturing delayed responses and dynamic interactions from real-world systems. | 1. Uses LSTM networks trained on real Building Automation System (BAS) data to approximate HVAC operational dynamics. 2. Employs DRL (specifically DDPG) agents trained in these LSTM-based environments to control Air Handling Units (AHUs). 3. Demonstrates improved energy efficiency and thermal comfort compared to rule-based control. | Subsystem | AHU | Component | Black-Box | Long Short-Term Memory (LSTM) neural networks | Historical BAS data approximates system behavior sufficiently for model training. | No | - | Yes | Real data | N/A | N/A | Virtual testbed | Three AHUs from a real office building, Each AHU serves a separate building section, Testbed environments were created using second-year BAS data | AHU | Component | Black-Box | Long Short-Term Memory (LSTM) neural networks | Historical BAS data approximates system behavior sufficiently for model training. | No | - | Yes | Real data | N/A | N/A | - | 15min | Fan speed, damper position, heating valve status, liquid solenoid status | Low | Energy consumption, Thermal comfort | Rule-Based Control (RBC) strategy implemented in the building | No | Simulation only | No | The process model (environment) and testbed are the same | ENERGY-CONSUMPTION; BUILDINGS; SYSTEMS; COMFORT; MODELS | [Zou, Zhengbo; Yu, Xinran; Ergan, Semiha] NYU, Dept Civil & Urban Engn, MetroTech Ctr 15, Brooklyn, NY 11201 USA | New York University | Zou, ZB (corresponding author), NYU, Dept Civil & Urban Engn, MetroTech Ctr 15, Brooklyn, NY 11201 USA. | zz1658@nyu.edu | 125 | 130 | 168 | [5 empty] | 106535
93 | 93 | Development, analysis and application of a predictive controller to a small-scale district heating system | Saletti, C; Gambarotta, A; Morini, M | Saletti, Costanza; Gambarotta, Agostino; Morini, Mirko | 2026-01-25 | 2020 | http://dx.doi.org/10.1016/j.applthermaleng.2019.114558 | Model Predictive Control; Dynamic programming; District heating and cooling network; Identification; Optimization | CO | Applied Thermal Engineering | Most MPC implementations are focused on HVAC systems of individual buildings without accounting for distribution network dynamics or scalable modular deployment. Existing methods often require high computational effort or ignore user-level dynamics in district systems. | 1. Develop a novel MPC framework based on a custom Dynamic Programming (DP) algorithm suitable for district heating systems. 2. Model the full DHC system, including distribution and building dynamics, in an integrated way. 3. Implement a modular, multi-agent control architecture. 4. Validate the controller via Model-in-the-Loop simulation of a school complex. | Subsystem | Indoor air temperature, District pipe network | Subsystem | Gray-Box | First-order discrete-time model | No solar/occupancy gains, Return temperature fixed at setpoint, No infiltration or forced ventilation | Yes | Energy use model | Yes | Simulated data | N/A | MATLAB | Virtual testbed | Simulation of a small DHC network serving two buildings | Indoor air temperature, District pipe network | Subsystem | White-Box | Lumped thermal energy balances for buildings and pipes | Uniform temperature in pipes (no PDEs) | Yes | boiler, substation, mixing valve | No | None | MATLAB ODE Solvers | MATLAB | - | 15min | Water mass flow rate, Mixing (supply) temperature | Medium | Fuel consumption, Temperature constraint satisfaction, Time advance in meeting comfort conditions | Conventional PID controller | No | Simulation only | Yes | Model representation limit | THERMAL-ENERGY STORAGE; ORGANIC RANKINE-CYCLE; BUILDING ENERGY; CONTROL STRATEGY; COMFORT MANAGEMENT; MODEL; OPTIMIZATION; NETWORKS; PERFORMANCE; SIMULATION | [Saletti, Costanza; Gambarotta, Agostino; Morini, Mirko] Univ Parma, Dept Engn & Architecture, Parco Area Sci 181-A, I-43124 Parma, Italy; [Gambarotta, Agostino; Morini, Mirko] Univ Parma, Ctr Energy & Environm CIDEA, Parco Area Sci 42, I-43124 Parma, Italy | University of Parma; University of Parma | Saletti, C (corresponding author), Univ Parma, Dept Engn & Architecture, Parco Area Sci 181-A, I-43124 Parma, Italy. | costanza.saletti@unipr.it | 33 | 34 | 165 | [5 empty] | 114558
94 | 94 | A computationally efficient method for fault diagnosis of fan-coil unit terminals in building Heating Ventilation and Air Conditioning systems | Ranade, A; Provan, G; Mady, AED; O'Sullivan, D | Ranade, Akshay; Provan, Gregory; Mady, Alie El-Din; O'Sullivan, Dominic | JAN | 2020 | http://dx.doi.org/10.1016/j.jobe.2019.100955 | Fault detection and diagnosis (FDD); Fan-coil units; Grey-box modelling; Regression modelling | FDD | Journal of Building Engineering | Existing FDD approaches primarily focus on central HVAC components (AHUs, chillers, boilers, VAVs), with limited attention to fan-coil units (FCUs). Furthermore, many methods rely on black-box models, which lack robustness and physical interpretability, often requiring complex mappings between model outputs and fault types. | 1. To develop a computationally efficient, grey-box model-based FDD method for FCUs. 2. To propose a residual generation technique using simplified heat exchanger models. 3. To demonstrate fault isolation through decision rules derived from residual patterns. 4. To provide a virtual testbed to simulate various fault scenarios for evaluation. | Subsystem | HX | Component | Gray-Box | First-order dynamics for outlet temperatures with polynomial regression for effectiveness approximation | Inlet water temperature is constant, Control signal affects both valve and fan proportionally | No | - | Yes | Simulated data | N/A | N/A | Virtual testbed | Simulated 2-pipe heating-mode FCU system with zone model (3R–2C wall dynamics), incorporating various faults: stuck fan/valve, heat exchanger fouling, zone temperature sensor bias. | Building thermal, HX | Subsystem | White-Box | Eff-NTU-based coil model with first-order dynamics, 3R2C zone model | Inlet water temperature is constant, Control signal affects both valve and fan proportionally, Flow rates are proportional to actuator positions, Zone air is well-mixed | Yes | Fan, Valve | Yes | Validated platform | Modelica Standard Library, Modelica Noise Library | Modelica | - | 3min | - | - | Residual magnitude (accuracy), Fault separability in residual space, Model execution time and memory footprint | Full nonlinear model of FCU coil (used for baseline) | No | Simulation only | Yes | Model representation limit | MODEL; PROGNOSTICS; ARX | [Ranade, Akshay; Provan, Gregory] Univ Coll Cork, Dept Comp Sci, Cork T12 XF62, Ireland; [Mady, Alie El-Din] Penrose Wharf Business Ctr, United Technol Res Ctr, Cork T23 XN53, Ireland; [O'Sullivan, Dominic] Univ Coll Cork, Dept Civil Engn, Cork T12 K8AF, Ireland | University College Cork; RTX Corporation; University College Cork | Ranade, A (corresponding author), Univ Coll Cork, Dept Comp Sci, Cork T12 XF62, Ireland. | akshay.ranade@ucc.ie; g.provan@cs.ucc.ie; madyaa@utrc.utc.com; dominic.osullivan@ucc.ie | 26 | 28 | 27 | [5 empty] | 100955
95 | 95 | Experimental study of model predictive control for an air-conditioning system with dedicated outdoor air system | Yang, SY; Wan, MP; Ng, BF; Dubey, S; Henze, GP; Chen, WY; Baskaran, K | Yang, Shiyu; Wan, Man Pun; Ng, Bing Feng; Dubey, Swapnil; Henze, Gregor P.; Chen, Wanyu; Baskaran, Krishnamoorthy | 2026-01-01 | 2020 | http://dx.doi.org/10.1016/j.apenergy.2019.113920 | Model predictive control; Separate sensible and latent cooling; Thermal comfort; Real-time control and optimization; Dedicated outdoor air system | CO | Applied Energy | While prior studies on DOAS-assisted SSLC systems demonstrated potential benefits in energy efficiency and indoor environmental control, most were based on simulation only. There was a lack of experimental validation of these systems, particularly under coordinated control schemes such as MPC. | 1. Develop a multi-objective MPC for DOAS-assisted SSLC systems that optimizes both energy efficiency and thermal comfort. 2. Experimentally validate the MPC strategy in a real lecture theatre by comparing it with a conventional BMS using feedback-based PID control. | Subsystem | Building thermal | Component | Gray-Box | linear state-space model | First-order RC model; furnishings excluded, No infiltration considered, Adjacent rooms’ heat transfer neglected | Yes | Indoor humidity, AHU, DOAS, (PMV) | Yes | Real data | N/A | MATLAB | Real building | Lecture Theatre 3 (LT3), 255 m², with 240 seats, converted from single-coil AHU to DOAS-assisted SSLC setup. Full real-time experimental setup at Nanyang Technological University, Singapore. | - | - | - | - | - | - | - | - | - | - | - | Sensors: EDS-MN-ENV-THPL, Delta OHM-TP3276.2, Delta OHM-AP3203.2, SIEMENS-PAC3200, SIEMENS-PAC3200, Schneider-SHD 101, Veris Industries-CD Series, SIEMENS-QVM62.1, Contrec-212, ABB-WaterMaster Series, ABB-TSC420, Delta OHM-HP3217.2R; Controller: Schneider AS-P; Modbus TCP/IP | 2min | Cooling power set-points for both the DOAS and AHU | Medium | Thermal comfort (PMV), Indoor humidity, Cooling energy consumption | Conventional BMS with PID control (baseline) | Yes | Full-scale real-world deployment | Yes | Model representation limit | THERMAL COMFORT; BUILDING ENERGY; TEMPERATURE; HUMIDITY; OPTIMIZATION; PERFORMANCE; MANAGEMENT; EFFICIENCY | [Yang, Shiyu; Wan, Man Pun; Ng, Bing Feng; Chen, Wanyu] Nanyang Technol Univ, Sch Mech & Aerosp Engn, Singapore 639798, Singapore; [Yang, Shiyu; Dubey, Swapnil; Baskaran, Krishnamoorthy] Nanyang Technol Univ, Energy Res Inst NTU ERI N, Singapore 637553, Singapore; [Henze, Gregor P.] Univ Colorado, Civil Environm & Architectural Engn, Boulder, CO 80309 USA | Nanyang Technological University; Nanyang Technological University; University of Colorado System; University of Colorado Boulder | Ng, BF (corresponding author), Nanyang Technol Univ, Sch Mech & Aerosp Engn, Singapore 639798, Singapore. | bingfeng@ntu.edu.sg | 61 | 64 | 257 | [5 empty] | 113920
96 | 96 | Modeling and Controlling of Temperature and Humidity in Building Heating, Ventilating, and Air Conditioning System Using Model Predictive Control | Bahramnia, P; Rostami, SMH; Wang, J; Kim, GJ | Bahramnia, Pouria; Hosseini Rostami, Seyyed Mohammad; Wang, Jin; Kim, Gwang-jun | 2026-12-02 | 2019 | http://dx.doi.org/10.3390/en12244805 | MPC; HVAC; BMS; energy saving; simultaneously control of temperature and humidity; constrained quadratic optimal control; multi-objective optimization | CO | Energies | Prior work focused mainly on temperature control. This study highlights the need for simultaneous control of temperature and humidity, aligning with ASHRAE standards. | 1. Develop a dynamic model for joint temperature and humidity behavior using physical laws. 2. Design an MPC controller to optimize thermal comfort and energy use. 3. Compare MPC performance to conventional PI control under varying sampling intervals. | Subsystem | Indoor air temperature, IAQ | Component | Gray-Box | Linearized state-space model derived from physical RC dynamics | Captures dominant system dynamics with reduced complexity | No | - | No | None | N/A | MATLAB | Virtual testbed | Simulated office room using detailed RC network modeling all walls, roof, windows, internal loads, and humidity exchange with external air | Building thermal, IAQ | Component | White-Box | RC network equations | Uniform distribution of T and H, Constant pressure, Linear wall-air heat transfer | No | - | No | None | N/A | MATLAB | - | 10min | Heater supply air temperature, Humidifier moisture ratio input | Medium | Tracking accuracy, Control effort (norms), Sampling time and energy-related implications | PI controller | No | Simulation only | Yes | Model representation limit | HVAC; ENERGY | [Bahramnia, Pouria] Islamic Azad Univ, Sci & Res Branch, Dept Elect Engn, Tehran 1477893855, Iran; [Hosseini Rostami, Seyyed Mohammad] Shiraz Univ Technol, Dept Elect Engn, Shiraz 7155713876, Fars, Iran; [Hosseini Rostami, Seyyed Mohammad] West Mazandaran Elect Power Distribut Co, Nowshahr 4651739948, Mazandaran, Iran; [Wang, Jin] Changsha Univ Sci & Technol, Sch Comp & Commun Engn, Hunan Prov Key Lab Intelligent Proc Big Data Tran, Changsha 410004, Hunan, Peoples R China; [Wang, Jin] Fujian Univ Technol, Sch Informat Sci & Engn, Fuzhou 350118, Fujian, Peoples R China; [Kim, Gwang-jun] Chonnam Natl Univ, Dept Comp Engn, Gwangju 61186, South Korea | Islamic Azad University; Shiraz University of Technology; Changsha University of Science & Technology; Fujian University of Technology; Chonnam National University | Kim, GJ (corresponding author), Chonnam Natl Univ, Dept Comp Engn, Gwangju 61186, South Korea. | pouria.bahramnia@srbiau.ac.ir; seyyed.mazandaran@gmail.com; jinwang@csust.edu.cn; kgj@chonnam.ac.kr | 30 | 31 | 12 | 24 |  |  |  |  | 4805
97 | 97 | Optimal Dispatch of Aggregated HVAC Units for Demand Response: An Industry 4.0 Approach | Short, M; Rodriguez, S; Charlesworth, R; Crosbie, T; Dawood, N | Short, Michael; Rodriguez, Sergio; Charlesworth, Richard; Crosbie, Tracey; Dawood, Nashwan | 2026-11-02 | 2019 | http://dx.doi.org/10.3390/en12224320 | industry 4.0; digitalization; demand response; HVAC control; dynamic programming; nonlinear optimization | EF | Energies | Existing DR schemes for small/medium buildings lack scalability, real-time efficiency, and precise control/settlement strategies. Most approaches assume large populations for statistical models and struggle with communication/computation loads, lacking rigorous baseline modeling. | 1. Propose a scalable, partially decentralized optimization framework for aggregated HVAC-based DR within an Industry 4.0 framework. 2. Develop a dynamic programming-based HVAC unit controller (ITU) for predictive dispatch. 3. Create a baseline estimation mechanism and an aggregator-level allocation/reallocation (UAS) algorithm for coordinated DR. | Subsystem | Indoor air temperature | Component | Gray-Box | Discrete-time state-space model | Heating/cooling is simplified to thermal gain/loss with fixed constants | No | - | Yes | Real data | N/A | N/A | Virtual testbed, Real building | Virtual: five simulated HVAC units; Real: Four rooftop HVAC/AHU units serving a large UK university building with both heating and cooling loads. BACNet-connected controller deployed as ITU for on-site predictive dispatch, DR event tested with 200 kWh curtailment in live building operation. | Indoor air temperature | Component | Gray-Box | Discrete-time state-space model | Heating/cooling is simplified to thermal gain/loss with fixed constants | No | - | Yes | Real data | N/A | N/A | BACNet, Programmable controllers as ITUs, IP-based communication with OpenADR/Web Services compatibility, Cloud-based aggregator | 1h | On/off signal to HVAC compressor or thermal unit | Low | Zone thermal comfort (temperature tracking), Electricity consumption during DR window, Baselining accuracy, Aggregated curtailment success, DR cost optimization | Baseline scenario (no DR), Other units with different DR allocation levels (40/100/160 kWh) | Yes | Full-scale real-world deployment | Yes, No | Model representation limit | DIRECT LOAD CONTROL; OPTIMIZATION; FUTURE | [Short, Michael; Rodriguez, Sergio; Crosbie, Tracey; Dawood, Nashwan] Teesside Univ, Sch Comp Engn & Digital Technol, Middlesbrough TS1 3BA, Cleveland, England; [Charlesworth, Richard] Siemens Plc, Energy Management Div, Princess Rd, Manchester M20 2UR, Lancs, England | University of Teesside; Siemens AG; Siemens United Kingdom | Short, M (corresponding author), Teesside Univ, Sch Comp Engn & Digital Technol, Middlesbrough TS1 3BA, Cleveland, England. | m.short@tees.ac.uk; S.Rodriguez@tees.ac.uk; Richard.Charlesworth@siemens.com; T.Crosbie@tees.ac.uk; n.n.dawood@tees.ac.uk | 16 | 16 | 12 | 22 |  |  |  |  | 4320
98 | 98 | Mapping the energy flexibility potential of single buildings equipped with optimally-controlled heat pump, gas boilers and thermal storage | D'Ettorre, F; De Rosa, M; Conti, P; Testi, D; Finn, D | D'Ettorre, Francesco; De Rosa, Mattia; Conti, Paolo; Testi, Daniele; Finn, Donal | OCT | 2019 | http://dx.doi.org/10.1016/j.scs.2019.101689 | Energy flexibility; Building; Smart grids; Thermal storage; Heat pump; Model predictive control | EF | Sustainable Cities and Society | The study addresses the lack of standardised methodologies for assessing the energy flexibility potential and associated costs in hybrid heat pump-gas boiler systems. Most previous work lacked integrated techno-economic assessments and did not quantify flexibility or its economic value comprehensively. | 1. Propose indicators to assess DR program performance. 2. Develop a control algorithm for hybrid systems (heat pump + boiler) to minimize cost and enable DR. 3. Evaluate different DR programs from a techno-economic and environmental perspective using performance maps. | Subsystem | TES | Component | White-Box | Lumped parameter | Perfect mixing in TES, TES thermal losses modeled using simplified heat loss equations | Yes | Heat pump, Gas boiler | No | None | CasADi, IPOPT | Python | Virtual testbed | Simulated single-building system in Trieste (Italy), with: Electrically-driven air-source heat pump (4 kW), Gas boiler, Water-based space heating TES (0.5 or 0.75 m³) | TES | Component | White-Box | Lumped parameter | Perfect mixing in TES, TES thermal losses modeled using simplified heat loss equations | Yes | Heat pump, Gas boiler | No | None | N/A | Python | - | 1h | Heat pump and boiler power input; TES charge/discharge | Medium | Operational cost, Primary energy consumption, Cost deviation and flexibility-specific cost (€/kWh shifted), SoC profile, energy shifting effectiveness | Cost-optimal control with no DR | No | Simulation only | No | The process model and testbed are the same | DEMAND-SIDE-MANAGEMENT; MODEL-PREDICTIVE CONTROL; SYSTEMS; OPTIMIZATION; SIMULATION; IMPACT; OPERATION; FRAMEWORK | [D'Ettorre, Francesco; Conti, Paolo; Testi, Daniele] Univ Pisa, Dept Energy Syst Terr & Construct Engn DESTEC, BETTER Bldg Energy Tech & Technol Res Grp, Pisa, Italy; [De Rosa, Mattia; Finn, Donal] Univ Coll Dublin, Sch Mech & Mat Engn, Dublin 4, Ireland; [De Rosa, Mattia; Finn, Donal] Univ Coll Dublin, UCD Energy Inst, Dublin 4, Ireland | University of Pisa; University College Dublin; University College Dublin | De Rosa, M (corresponding author), Univ Coll Dublin, Sch Mech & Mat Engn, Dublin 4, Ireland.;De Rosa, M (corresponding author), Univ Coll Dublin, UCD Energy Inst, Dublin 4, Ireland. | francesco.dettorre@ing.unipi.it; mattia.derosa@ucd.ie; paolo.conti@unipi.it; daniele.testi@unipi.it; donal.finn@ucd.ie | 58 | 60 | 50 | [5 empty] | 101689
99 | 99 | A predictive control strategy for optimal management of peak load, thermal comfort, energy storage and renewables in multi-zone buildings | Biyik, E; Kahraman, A | Biyik, Emrah; Kahraman, Aysegul | SEP | 2019 | http://dx.doi.org/10.1016/j.jobe.2019.100826 | Building energy management; Optimization; Model predictive control; HVAC systems; Battery energy storage; Photovoltaics; Demand response | EF | Journal of Building Engineering | Existing smart HVAC control solutions are difficult to scale, require extensive modeling or new hardware, and often fail to coordinate DERs (e.g., PV, batteries) with HVAC systems for DR and comfort optimization. There's a lack of practical, low-cost solutions for multi-zone control in retrofitted buildings. | 1. Develop a low-complexity, data-driven multi-zone thermal model for buildings. 2. Design an MPC controller that: -Indirectly controls HVAC via thermostat setpoints. -Coordinates battery energy storage (BES) and PV. -Minimizes peak load and energy cost. -Ensures human thermal comfort using Fanger’s PPD model. | Subsystem | Building thermal, BES | Component | Gray-Box, White-Box | Lumped RC model; Battery storage system: energy balance, simple first order system | No inter-zone dynamics modeled. HVAC power is direct input. | Yes | PV, (PPD) | Yes | Real data | N/A | MATLAB | Virtual testbed | Simulated model of 4-zone real building (Yasar University) | Building thermal, BES | Component | Gray-Box, White-Box | Lumped RC model; Battery storage system: energy balance, simple first order system | No inter-zone dynamics modeled. HVAC power is direct input. | Yes | PV, (PPD) | Yes | Real data | Simulink | MATLAB | - | 15min | Thermostat setpoints, Battery charging/discharging, Renewable power utilization | High, Medium | Peak load reduction, Energy cost savings, Thermal comfort (PPD), Battery cycling minimization | Baseline fixed 22°C thermostat strategy, Cases with and without BES/PV | No | Simulation only | No | The process model and testbed are the same | OPTIMAL TEMPERATURE CONTROL; DEMAND RESPONSE; CONTROL-SYSTEMS; OPTIMIZATION; RELIABILITY; CONSUMPTION | [Biyik, Emrah; Kahraman, Aysegul] Yasar Univ, Dept Energy Syst Engn, Univ Cd 37-39, Izmir, Turkey | Yasar University | Biyik, E (corresponding author), Yasar Univ, Dept Energy Syst Engn, Univ Cd 37-39, Izmir, Turkey. | emrah.biyik@yasar.edu.tr; aysegul.kahraman@yasar.edu.tr | 79 | 84 | 25 | [5 empty] | 100826
100 | 100 | Data-driven model predictive control for building climate control: Three case studies on different buildings | Wang, JY; Li, S; Chen, HX; Yuan, Y; Huang, Y | Wang, Jiangyu; Li, Shuai; Chen, Huanxin; Yuan, Yue; Huang, Yao | AUG | 2019 | http://dx.doi.org/10.1016/j.buildenv.2019.106204 | Data-driven predictive control; Deep learning; Resistancecapacity model; Building climate control; Optimization algorithm | CO | Building and Environment | 1. Traditional MPC relies on grey-box models (e.g., RC models) that require time-consuming parameter estimation, expert knowledge, and high modeling costs. 2. These models are not easily transferable to buildings with different geometries or conditions. 3. Applying nonlinear data-driven models to MPC is challenging due to non-convexity in optimization. | 1. Develop a hybrid optimization algorithm (BSAS-LM) for nonlinear/non-convex data-driven predictive control (DDPC). 2. Validate the feasibility and scalability of DDPC using different data-driven models (ARX, SVR, ANN, MLP) in three different building configurations. 3. Demonstrate application of DDPC in three climate control scenarios: constant setpoint, lowered setpoint, and pre-heating. | Subsystem | Indoor air temperature | Component | Gray-Box, Black-Box | Case #1: RC, ARX, SVR, ANN; Case #2 & #3: MLP | RC model: Linear time-invariant (LTI), three-node (wall, indoor, internal mass), split solar gain with α parameter; Black-box: No solar gain calculation; uses measurable inputs like sky illuminance and wind speed | No | - | Yes | Simulated data | N/A | Python | Virtual testbed | Case #1: Single-zone building, electric heater (3 kW); Case #2: 3-floor building with 3 electric heaters (15, 12, 12 kW); Case #3: One-story, 3-zone building (6, 4, 4 kW heaters) | Building thermal | Component | White-Box | EnergyPlus-based model | Standard EnergyPlus modeling | No | - | Yes | Validated platform | EnergyPlusToFMU | EnergyPlus | - | 15min | Heating power of electric heaters | Low | Temperature tracking accuracy; Control signal smoothness; Oscillation analysis | RC-based MPC using ECOS solver | No | Simulation only | Yes | Model representation limit | ARTIFICIAL NEURAL-NETWORK; ENERGY; OPTIMIZATION; TEMPERATURE; SYSTEMS; MPC; ALGORITHM; SAVINGS | [Wang, Jiangyu; Chen, Huanxin; Huang, Yao] Huazhong Univ Sci & Technol, Sch Energy & Power Engn, Dept Refrigerat & Cryogen Engn, Wuhan, Hubei, Peoples R China; [Li, Shuai] Hong Kong Polytech Univ, Dept Comp, Kowloon, Hong Kong, Peoples R China; [Yuan, Yue] Huazhong Univ Sci & Technol, China EU Inst Clean & Renewable Energy, Wuhan, Hubei, Peoples R China | Huazhong University of Science & Technology; Hong Kong Polytechnic University; Huazhong University of Science & Technology | Chen, HX (corresponding author), Huazhong Univ Sci & Technol, Sch Energy & Power Engn, Dept Refrigerat & Cryogen Engn, Wuhan, Hubei, Peoples R China. | chenhuanxin@tsinghua.org.cn | 52 | 55 | 160 | [5 empty] | 106204
101 | 101 | Modeling and fault diagnosis design for HVAC systems using recurrent neural networks | Shahnazari, H; Mhaskar, P; House, JM; Salsbury, TI | Shahnazari, Hadi; Mhaskar, Prashant; House, John M.; Salsbury, Timothy, I | 2026-07-12 | 2019 | http://dx.doi.org/10.1016/j.compchemeng.2019.04.011 | Fault diagnosis; Recurrent neural networks; Actuator faults; Sensor faults; HVAC systems | FDD | Computers & Chemical Engineering | Most existing HVAC fault detection and diagnosis methods either depend on mechanistic models (which are hard to develop and maintain) or require extensive fault history and heuristic rule sets. Many fail to capture system nonlinearities or are not scalable to multi-zone systems. | 1. Develop a recurrent neural network (RNN)-based modeling framework for HVAC systems. 2. Design a fault detection and isolation (FDI) strategy using only healthy data and no need for plant fault history. 3. Construct a distributed FDI architecture using local models and estimators that communicate across subsystems. | Subsystem | AHU | Component | Black-Box | Layer Recurrent Neural Networks (LRNs) | BIBO (bounded-input, bounded-output) system stability, Healthy operating data sufficiently represent typical system dynamics, Faults do not occur during training | No | - | Yes | Simulated data, Real data | N/A | N/A | Virtual testbed, Historical data | Simulation: 5-zone HVAC system modeled in Modelica, including AHU and VAV components; Real-world data: From Iowa Energy Center’s Energy Resource Station (ERS) with 2 AHUs and 4 zones per AHU. | AHU | Component | White-Box | First-principles Modelica-based simulation | HVAC physics with known control architecture | No | - | Yes | Validated platform | N/A | Modelica | - | N/A | - | - | Residual sensitivity and threshold robustness, Ability to detect and isolate single and multiple faults, Comparison of estimation accuracy | Subspace identification-based models for FDI, LRNs vs. subspace models in fault detection sensitivity | No | Simulation only, Historical data | Yes | Model representation limit | OPTIMIZATION; ACTUATOR | [Shahnazari, Hadi; Mhaskar, Prashant] Dept Chem Engn, 1280 Main St West, Hamilton, ON L8S 4L7, Canada; [House, John M.] Johnson Controls Int Plc, Bldg Management Syst Res Grp, Montreal, PQ, Canada; [Salsbury, Timothy, I] Johnson Controls Int Plc, Bldg Management Syst Res Grp, Milwaukee, WI 53202 USA |  | Mhaskar, P (corresponding author), Dept Chem Engn, 1280 Main St West, Hamilton, ON L8S 4L7, Canada. | shahnah@mcmaster.ca; mhaskar@mcmaster.ca; timothy.i.salsbury@jci.com | 90 | 92 | 126 |  |  |  | 189 | 203
102 | 102 | A model predictive control strategy to optimize the performance of radiant floor heating and cooling systems in office buildings | Joe, J; Karava, P | Joe, Jaewan; Karava, Panagiota | 2026-07-01 | 2019 | http://dx.doi.org/10.1016/j.apenergy.2019.03.209 | Radiant floor system; Thermally Activated Building Systems (TABS); Model predictive control; Field implementation | CO | Applied Energy | 1. Prior studies on MPC for radiant systems relied mostly on simulation or confined testbeds, lacking real-world implementations. 2. Existing MPC formulations often involve heuristic weights in nonlinear optimization, limiting generalizability and robustness. 3. Lack of reliable, validated building models using real building data undermines prior results. | 1. Develop and implement a real-time MPC strategy for radiant floor systems in a real office building. 2. Use data-driven models validated on actual building data. 3. Demonstrate the energy and cost savings potential under realistic operating conditions. | Whole System | Building thermal | Component | Gray-Box | State-space formulation with a grey-box model (5 thermal states) | Concrete slab is divided into thermal nodes (surface, core, insulation), External disturbances modeled via empirical coefficients | Yes | Chiller | Yes | Real data | N/A | MATLAB | Real building | Three open-plan office spaces at Purdue's Herrick Labs; one equipped with radiant floor system and two with air delivery for comparative study. | - | - | - | - | - | - | - | - | - | - | - | RTD sensors (ACI, A/TT1K-LTS), Flow meter (ONICOM), RTD sensors (Digi-Key, 10 K Ω), Thermocouples (Omega, T-type), Pyranometer (LI-COR 200-SL), BMS with Niagara/AX software framework, JACE controllers, Modbus | 30min | Heating/cooling rate to slab via PLR | Low | HVAC energy consumption, Cost savings, Thermal comfort | Feedback control (on-off and PI), Air delivery system with/without MPC, Simulated MPC (ideal vs. implemented) | Yes | Full-scale real-world deployment | Yes | Model representation limit | THERMAL MASS; ENERGY; DEMAND; TABS; IDENTIFICATION; MANAGEMENT; COMFORT; LOAD | [Joe, Jaewan; Karava, Panagiota] Purdue Univ, Lyles Sch Civil Engn, 550 Stadium Mall Dr, W Lafayette, IN 47907 USA; [Joe, Jaewan; Karava, Panagiota] Purdue Univ, Ctr High Performance Bldg, Ray W Herrick Labs, 140 S Martin Jischke Dr, W Lafayette, IN 47907 USA | Purdue University System; Purdue University; Purdue University System; Purdue University | Karava, P (corresponding author), Purdue Univ, Lyles Sch Civil Engn, 550 Stadium Mall Dr, W Lafayette, IN 47907 USA. | pkarava@purdue.edu | 158 | 166 | 245 |  |  |  | 65 | 77
103 | 103 | Model predictive control for thermal energy storage and thermal comfort optimization of building demand response in smart grids | Tang, R; Wang, SW | Tang, Rui; Wang, Shengwei | 2026-05-15 | 2019 | http://dx.doi.org/10.1016/j.apenergy.2019.03.038 | Model predictive control (MPC); Linear state-space model; Air-conditioning system; Demand side management; PCM tank; Indoor thermal comfort | EF | Applied Energy | The study addresses the lack of online optimal control strategies for central air-conditioning systems integrated with active cold storage during fast demand response (DR) events. While prior work has explored day-ahead DR control or cold storage sizing, few have tackled real-time optimization balancing both grid requirements and indoor comfort. | 1. Develop an MPC-based strategy for fast DR events that optimizes chiller power demand and cold storage discharge. 2. Incorporate a simplified yet effective linear state-space model with self-correction. 3. Achieve both maximum power reduction and acceptable indoor thermal comfort in real-time. | Whole System | Building thermal | Component | Gray-Box | Linear state-space 2R2C model | Parameters like COP, solar absorptance, and internal gains are constant during the short (2h) DR event. | Yes | Chiller | Yes | Simulated data | YALMIP, Gurobi | MATLAB | Virtual testbed | A TRNSYS-based dynamic simulation platform modeling a real super high-rise building's HVAC system in Hong Kong | HVAC system | Whole System | White-Box | TRNSYS physical modeling of chillers, cold storage, pumps, AHUs, and zones | High-fidelity model, no major simplifying assumptions beyond library defaults. | No | - | Yes | Real data | N/A | TRNSYS | - | 15min | Chiller power demand, Cooling discharge rate of cold storage | Medium | Max indoor air temperature, Chiller power demand stability (standard deviation), Unmet comfort duration, Energy discharged from storage | Two reference cases without MPC: Constant storage discharge + fixed chiller demand; Constant storage discharge + relaxed indoor temp control | No | Simulation only | Yes | Model representation limit | DIRECT LOAD CONTROL; AIR-CONDITIONING SYSTEMS; CONTROL STRATEGY; URGENT REQUESTS; TEMPERATURE; PERFORMANCE; EFFICIENCY; MASS | [Tang, Rui; Wang, Shengwei] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China | Hong Kong Polytechnic University | Wang, SW (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | beswwang@polyu.edu.hk | 127 | 140 | 242 |  |  |  | 873 | 882
104 | 104 | Modelling and predictive control of a solar cooling plant with flexible configuration | Rathod, N; La Bella, A; Puleo, G; Scattolini, R; Rossetti, A; Sandroni, C | Rathod, Niraj; La Bella, Alessio; Puleo, Gianluca; Scattolini, Riccardo; Rossetti, Andrea; Sandroni, Carlo | APR | 2019 | http://dx.doi.org/10.1016/j.jprocont.2019.01.009 | Solar cooling plant; Modelling; Model identification; Model Predictive Control (MPC); Hybrid systems | CO | Journal of Process Control | The paper addresses the need for efficient control strategies for hybrid-configured solar cooling systems that integrate various energy sources (solar and gas) and storage elements. It highlights challenges in dynamically managing such plants under weather variability and user demand, especially given the complexity from discrete (on/off valves) and continuous (pumps) controls. | 1. Develop a detailed dynamic model of a solar cooling plant using first-principles and data-driven techniques. 2. Design and implement a Hybrid Model Predictive Control (HMPC) system to optimally manage the plant's configuration. 3. Validate both the model and control strategy in simulations and real-world experiments to demonstrate performance benefits in energy efficiency. | Subsystem | Chiller | Component | Black-Box | Reduced-order first-order transfer functions fitted to simulation step responses. Model expressed as Mixed Logical Dynamical (MLD) system discretized at 15-minute intervals. | Time-invariant linear dynamics per configuration and flow rate. Finite set of hot water flow rates discretized into 4 levels. Dynamics represented using first-order transfer functions per operating mode. | No | - | Yes | Simulated data | YALMIP, CPLEX, Hysdel | MATLAB | Virtual testbed, Real building | Virtual testbed: High-fidelity nonlinear plant model, built in MATLAB/Simulink using physical principles and validated with real operational data. Real building: Experimental solar cooling plant at RSE, Milan, equipped with sensors, parabolic collectors, absorption chiller, and tanks. | Solar collector, TES, HVAC pipe network | Subsystem | Gray-Box | Full thermohydraulic behavior: solar collector, tanks, pipes | Uniform tank temperature, Neglected chiller internal thermal inertia, Fixed cold water pump speed when active, Autonomous user-side valve control | Yes | Chiller, Pump | Yes | Real data | Simulink | MATLAB | N/A | 15min | Hot water flow rate (pump), Chiller status (on/off, gas mode), Tank inclusion (valve control for hot/cold storage) | Medium | Gas consumption, Electric energy consumption, Compliance with temperature bounds, Flexibility (mode switching, storage use) | Relay-based control strategy with fixed thresholds and no forecast-based optimization | Yes | Full-scale real-world deployment | Yes | Model representation limit | SYSTEMS; MANAGEMENT; LOGIC | [Rathod, Niraj; La Bella, Alessio; Puleo, Gianluca; Scattolini, Riccardo] Politecn Milan, Dipartimento Elettron Informaz & Bioingn, Via Ponzio 34-5, I-20133 Milan, Italy; [Rossetti, Andrea; Sandroni, Carlo] Ric Sistema Energet, Power Generat Technol & Mat Dept, Via R Rubattino 54, I-20134 Milan, Italy | Polytechnic University of Milan | La Bella, A (corresponding author), Politecn Milan, Dipartimento Elettron Informaz & Bioingn, Via Ponzio 34-5, I-20133 Milan, Italy. | niraj.rathod@mail.polimi.it; alessio.labella@polimi.it; gianluca.puleo@mail.polimi.it; riccardo.scattolini@polimi.it; andrea.rossetti@rse-web.it; carlo.sandroni@rse-web.it | 12 | 12 | 76 |  |  |  | 74 | 86
105 | 105 | A model-based control strategy to recover cooling energy from thermal mass in commercial buildings | Shan, K; Wang, JY; Hu, MM; Gao, DC | Shan, Kui; Wang, Jiayuan; Hu, Maomao; Gao, Dian-ce | 2026-04-01 | 2019 | http://dx.doi.org/10.1016/j.energy.2019.02.045 | HVAC; Building thermal mass; Building energy conservation; Energy recovery; Demand limiting | EF | Energy | Few prior studies focus specifically on recovering stored cooling energy from building thermal mass, as opposed to more common applications like load shifting or peak demand limiting. Existing models are often complex, require detailed parameters, and are difficult to implement in real applications. | 1. Propose a practical, model-based control strategy to recover cooling energy stored in building thermal mass during office hours. 2. Develop a hybrid prediction model combining a simplified RC model and a black-box regression model. 3. Validate feasibility via on-site tests in a real commercial high-rise and simulation tests. | Subsystem | Building thermal | Component | Gray-Box | Simplified RC model (first-order differential equations), Multiple linear regression model, Combined via a data fusion algorithm | No interaction among zones in multi-zone scenario | No | - | Yes | Real data | N/A | N/A | Real building, Virtual testbed | Real: Three adjacent floors (17th–19th) of a 108-story super high-rise office building in Hong Kong (~3600 m²/floor, 2250 m² air-conditioned area per floor); Virtual: TRNSYS-based platform with Type 56 multi-zone model, AHU cooling coil, occupancy reader | Building thermal | Component | White-Box | TRNSYS Type 56 | Standard TRNSYS modeling | Yes | AHU | Yes | Real data | N/A | TRNSYS | N/A | N/A | AHU supply fan speed, AHU supply air temperature set-point | Low, Medium | Energy savings, Reduction in cooling demand, Room temperature change | Conventional HVAC control strategy on same building | Yes | Full-scale real-world deployment | Yes | Model representation limit | PARAMETER-ESTIMATION; DEMAND RESPONSE; PERFORMANCE; SYSTEMS | [Shan, Kui; Wang, Jiayuan] Shenzhen Univ, Sch Civil Engn, Shenzhen, Peoples R China; [Shan, Kui; Hu, Maomao] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Hong Kong, Peoples R China; [Gao, Dian-ce] Sun Yat Sen Univ, Sch Intelligent Syst Engn, Guangzhou, Guangdong, Peoples R China; [Gao, Dian-ce] Guangdong Prov Key Lab Fire Sci & Technol, Guangzhou, Guangdong, Peoples R China | Shenzhen University; Hong Kong Polytechnic University; Sun Yat Sen University | Gao, DC (corresponding author), Sun Yat Sen Univ, Sch Intelligent Syst Engn, Guangzhou, Guangdong, Peoples R China. | gaodiance@126.com | 36 | 36 | 172 |  |  |  | 958 | 967
106 | 106 | Optimal and near-optimal indoor temperature and humidity controls for direct load control and proactive building demand response towards smart grids | Tang, R; Wang, SW; Shan, K | Tang, Rui; Wang, Shengwei; Shan, Kui | DEC | 2018 | http://dx.doi.org/10.1016/j.autcon.2018.09.020 | Temperature control; Humidity control; Fast demand response; Direct load control; Genetic algorithm; Smart grid | EF | Automation in Construction | Conventional feedback control strategies fail under fast demand response (DR) events due to limited cooling supply, leading to unacceptably high indoor temperature and relative humidity. No previous study effectively addressed air-side control strategies for both temperature and humidity during DR events. | The paper develops and compares two strategies — an optimal control strategy based on model-predictive control and GA optimization, and a near-optimal empirical strategy — to optimize AHU airflow settings during DR events while satisfying power limiting thresholds and maintaining indoor thermal comfort (temperature and RH). | Whole System | Indoor air temperature, IAQ | Component | White-Box | Physics-based models (heat and mass transfer equations) | Lumped air volume with ideal mixing | Yes | Fan, Chiller, AHU | Yes | Previous Literature | N/A | MATLAB | Virtual testbed | A TRNSYS-based high-rise commercial building model with detailed subsystems (chillers, pumps, fans, AHUs, air ducts). Six thermal zones (1200–2400 m²), varied cooling loads, office hours 08:00–18:00, DR event from 14:00–16:00 on a typical Hong Kong summer day. | HVAC system | Whole System | White-Box | Detailed TRNSYS physics-based modeling of central HVAC systems and building envelope | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | 1min | Setpoints for air flow rates of each AHU fan | Medium | Indoor air temperature, Indoor relative humidity, Fan power savings, Dehumidification effectiveness | Conventional feedback control (static pressure reset) | No | Simulation only | Yes | Model representation limit | AIR-CONDITIONING SYSTEMS; CONTROL STRATEGY; THERMAL COMFORT; URGENT REQUESTS; DYNAMIC SIMULATION; GENETIC ALGORITHMS; CHALLENGES; OPTIMIZATION; DESIGN | [Tang, Rui; Wang, Shengwei; Shan, Kui] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China; [Wang, Shengwei] Hong Kong Polytech Univ, Res Inst Sustainable Urban Dev, Kowloon, Hong Kong, Peoples R China | Hong Kong Polytechnic University; Hong Kong Polytechnic University | Wang, SW (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | shengwei.wang@polyu.edu.hk | 24 | 25 | 96 |  |  |  | 250 | 261
107 | 107-A | Experimental Demonstration of Frequency Regulation by Commercial Buildings Part I: Modeling and Hierarchical Control Design | Vrettos, E; Kara, EC; MacDonald, J; Andersson, G; Callaway, DS | Vrettos, Evangelos; Kara, Emre C.; MacDonald, Jason; Andersson, Goran; Callaway, Duncan S. | JUL | 2018 | http://dx.doi.org/10.1109/TSG.2016.2628897 | Ancillary services; frequency control; demand response; commercial building; HVAC system; MPC | EF | IEEE Transactions on Smart Grid | There has been limited experimental verification of commercial buildings participating in frequency regulation markets. Most prior work has been simulation-based, focused on load shifting or peak shaving, and did not address implementation challenges such as model mismatch, forecast errors, and communication delays. | The study aims to experimentally demonstrate frequency regulation from a commercial building testbed, addressing the following: 1. A priori determination of reserve capacity and baseline power. 2. Balancing energy consumption and reserve provision for profitability and comfort. 3. Accurate real-time tracking of the regulation signal. 4. Development and validation of a three-level hierarchical control system using robust optimization and MPC. | Whole System | Building thermal | Component | Gray-Box | 2-state RC (resistance-capacitance) network thermal model with bilinear dynamics and Kalman filter. | Lumped air volume with ideal mixing | Yes | Fan | Yes | Lab | YALMIP | MATLAB | Lab | FLEXLAB at LBNL with two thermally identical and isolated building cells (1A and 1B), each 60 m². HVAC consists of dedicated AHUs with fan-based airflow control (no dampers), representative of 1980s commercial building construction. | - | - | - | - | - | - | - | - | - | - | - | Central Working Station, LabVIEW, TestStand National Instruments user interface, DNP3 protocol, Siemens Jetstream gateway, SQL database | Level 1 (reserve): Daily, Level 2 (MPC): Every 15 minutes, Level 3 (regulation control): Every 4 seconds | Level 1 (reserve): reserve capacity & baseline air flow, Level 2 (MPC): airflow setpoints, Level 3 (regulation control): fan speed | Low, Medium, High | Reserve capacity tracking, Energy consumption, Occupant comfort | PI control, Comparative models with 1-step vs 1-day ahead prediction, and 1-state vs 2-state models. | Partial | Lab setup | Yes | Model representation limit | HVAC CHILLER CONTROL; ANCILLARY SERVICE; DEMAND RESPONSE; ENERGY; AGGREGATIONS; RESERVES | [Vrettos, Evangelos; Andersson, Goran] Swiss Fed Inst Technol, Power Syst Lab, CH-8092 Zurich, Switzerland; [Kara, Emre C.] Lawrence Berkeley Natl Lab, Berkeley, CA 94720 USA; [Kara, Emre C.] SLAC Natl Accelerator Lab, Grid Integrat Syst & Mobil GISMo Grp, Menlo Pk, CA 94025 USA; [MacDonald, Jason] Lawrence Berkeley Natl Lab, Grid Integrat Grp, Berkeley, CA 94720 USA; [Callaway, Duncan S.] Univ Calif Berkeley, Energy & Resources Grp, Berkeley, CA 94720 USA | Swiss Federal Institutes of Technology Domain; ETH Zurich; United States Department of Energy (DOE); Lawrence Berkeley National Laboratory; Stanford University; United States Department of Energy (DOE); SLAC National Accelerator Laboratory; United States Department of Energy (DOE); Lawrence Berkeley National Laboratory; University of California System; University of California Berkeley | Vrettos, E (corresponding author), Swiss Fed Inst Technol, Power Syst Lab, CH-8092 Zurich, Switzerland. | vrettos@eeh.ee.ethz.ch; emrecan@slac.stanford.edu; jsmacdonald@lbl.gov; andersson@eeh.ee.ethz.ch; dcal@berkeley.edu | 80 | 92 | 9 | 4 |  |  | 3213 | 3223
| 107-B | Experimental Demonstration of Frequency Regulation by Commercial Buildings—Part II: Results and Performance Evaluation | Vrettos, E; Kara, EC; MacDonald, J; Andersson, G; Callaway, DS | Vrettos, Evangelos; Kara, Emre C.; MacDonald, Jason; Andersson, Goran; Callaway, Duncan S. | JUL | 2018 | http://dx.doi.org/10.1109/TSG.2016.2628893 | Buildings; Frequency control; Fans; Weather forecasting; Heating; MATLAB
108 | 108 | Hierarchical control of building HVAC system for ancillary services provision | Qureshi, FA; Jones, CN | Qureshi, Faran A.; Jones, Colin N. | 2026-06-15 | 2018 | http://dx.doi.org/10.1016/j.enbuild.2018.03.004 | Demand response; Ancillary services; Building control; HVAC modeling and control; Secondary frequency control; Smart grids; Robust optimizations; MPC | EF | Energy and Buildings | Existing work on demand-side ancillary services using HVAC systems often neglects the nonlinear dynamics of HVAC equipment, focuses only on building thermodynamics, or simplifies the chiller as having a constant coefficient of performance (COP). Moreover, complete strategies to control the full HVAC system (not just zones) for secondary frequency control are lacking. | The paper proposes a hierarchical control strategy for HVAC systems to provide secondary frequency regulation. The goal is to decouple building zone and HVAC system control, leverage robust optimization, and maximize electrical flexibility while maintaining occupant comfort. | Whole System | Building thermal, TES | Component | Gray-Box, White-Box | RC model, Energy balances for thermal storage | HVAC pipes/ducts are lossless, Stratified water tank modeled with two lumped temperature layers (warm/cold) | Yes | Chiller, Heat exchanger, Fan, Air mixer | Yes | Simulated data | OpenBuild Toolbox, YALMIP, CasADi | MATLAB | Virtual testbed | A standard 5-zone commercial office building from the U.S. DOE reference set (ASHRAE standard model) | Building thermal | Component | White-Box | EnergyPlus-based model | EnergyPlus model reduced to RC form for zone dynamics | Yes | HVAC system | Yes | Validated platform | N/A | EnergyPlus | - | 15min | Zone temperature setpoints, Chiller supply temperature, air supply temperature, mass flow rates | Medium, High | Provided flexibility, Tracking error of regulation signal, COP trajectories, Occupant discomfort | Fixed supply temperature strategy, Scenarios with/without thermal storage | No | Simulation only | Yes | Model representation limit | FREQUENCY REGULATION; ENERGY; MANAGEMENT; SIMULATION | [Qureshi, Faran A.; Jones, Colin N.] Ecole Polytech Fed Lausanne, Automat Control Lab, CH-1015 Lausanne, Switzerland | Swiss Federal Institutes of Technology Domain; Ecole Polytechnique Federale de Lausanne | Qureshi, FA (corresponding author), Ecole Polytech Fed Lausanne, Automat Control Lab, CH-1015 Lausanne, Switzerland. | faran.qureshi@epfl.ch; colin.jones@epfl.ch | 40 | 41 | 169 |  |  |  | 216 | 227
109 | 109 | Reconfigurable Model Predictive Control for Multievaporator Vapor Compression Systems | Burns, DJ; Danielson, C; Zhou, JQ; Di Cairano, S | Burns, Daniel J.; Danielson, Claus; Zhou, Junqiang; Di Cairano, Stefano | MAY | 2018 | http://dx.doi.org/10.1109/TCST.2017.2701772 | Model predictive control; plug-and-play (PnP) control; reconfigurable control; vapor compression systems (VCSs) | CO | IEEE Transactions on Control Systems Technology | Conventional MPC approaches for multievaporator vapor compression systems (ME-VCSs) require a separate controller for each possible configuration (each combination of ON/OFF evaporators), which is computationally and memory intensive. Prior work has not addressed the dynamic reconfiguration of MPC in response to ON/OFF changes in evaporators. | The study proposes a reconfigurable MPC framework that: 1. Can adapt online to different configurations (i.e., changing which evaporators are ON or OFF). 2. Minimizes memory storage by modifying only the cost function matrices. 3. Maintains closed-loop stability and constraint enforcement across configurations. 4. Demonstrates comparable performance to individual MPCs, validated in both simulation and experiments. | Subsystem | VCS | Subsystem | Black-Box | Linear state-space model identified from step response data; Hankel singular value decomposition for model reduction | Linear dynamics around operating points | No | - | Yes | Lab | N/A | N/A | Lab | A physical two-zone VCS testbed installed in insulated chambers with controlled heat injection and boundary conditions (e.g., 35°C outdoor air, 1.6kW heat loads). The VCS includes one outdoor unit and two indoor evaporator units. | - | - | - | - | - | - | - | - | - | - | - | N/A | 1min | Compressor frequency (CF), outdoor fan speed (ODF), cooling capacity commands (CCC1, CCC2) | Low | Tracking error (zone temperatures, discharge temp), Constraint satisfaction (e.g., Td ≤ Td_max), Memory usage and parameter efficiency | Collection of separately designed MPCs for fixed configurations | Partial | Lab setup | Yes | Model representation limit | PLUG | [Burns, Daniel J.; Danielson, Claus; Di Cairano, Stefano] Mitsubishi Elect Res Labs, Cambridge, MA 02139 USA; [Zhou, Junqiang] GE Global Res, One Res Circle, Niskayuna, NY 12309 USA | General Electric | Burns, DJ (corresponding author), Mitsubishi Elect Res Labs, Cambridge, MA 02139 USA. | burns@merl.com; danielson@merl.com; junqiang.zhou@ge.com; dicairano@merl.com | 14 | 14 | 26 | 3 |  |  | 984 | 1000
110 | 110 | Fault detection and diagnosis for nonlinear systems: A new adaptive Gaussian mixture modeling approach | Karami, M; Wang, LP | Karami, Majid; Wang, Liping | 2026-05-01 | 2018 | http://dx.doi.org/10.1016/j.enbuild.2018.02.032 | Gaussian mixture model; Unscented Kalman filter; Multi-chiller plant; Fault detection and diagnosis | FDD | Energy and Buildings | Existing fault detection and diagnosis (FDD) approaches for HVAC systems often rely on either static models or require multiple models for each fault type. Many machine learning methods lack adaptability to time-varying system behavior and struggle with simultaneous fault detection. There is also a lack of generalizable, single-model approaches that can both detect and diagnose various faults in a chiller system without excessive modeling effort. | The study proposes an Adaptive Gaussian Mixture Model (AGMM) method combining Gaussian Mixture Model Regression (GMMR) with an Unscented Kalman Filter (UKF) to: 1. Dynamically model nonlinear chiller system behavior. 2. Automatically detect and diagnose faults (including simultaneous faults) in a multi-chiller plant. 3. Reduce modeling burden by relying on a single fault-free data-driven model rather than multiple fault-specific models. | Subsystem | Chiller | Component | Black-Box | Gaussian Mixture Model Regression (GMMR) combined with Unscented Kalman Filter (UKF) | Nonlinear, multi-modal system behavior can be captured via GMM clusters. Model parameters adapt over time to reflect system changes. Training data is representative of fault-free operation. | No | - | Yes | Simulated data | N/A | N/A | Virtual testbed | A simulated all-variable-speed, water-cooled multi-chiller plant located in Berkeley, CA. Includes 3 chillers, air handling units, cooling towers, pumps, and PID controllers for pumps and fans. | Chiller plant | Subsystem | White-Box | Modelica-based models | Standard Modelica modeling | No | - | Yes | Validated platform | N/A | Modelica | - | 10min | - | - | Fault detection and diagnosis accuracy (parameter-based thresholds and detection delay) | Compared to ARX and RLS-ARX models. | No | Simulation only | Yes | Model representation limit | BUILDING SYSTEMS; REGRESSION; STRATEGY; PROGNOSTICS | [Karami, Majid; Wang, Liping] Univ Wyoming, Civil & Architectural Engn Dept, Laramie, WY 82071 USA | University of Wyoming | Wang, LP (corresponding author), Univ Wyoming, Civil & Architectural Engn Dept, Laramie, WY 82071 USA. | lwang12@uwyo.edu | 56 | 60 | 166 |  |  |  | 477 | 488
111 | 111 | Design and construction of a non-linear model predictive controller for building's cooling system | Erfani, A; Rajabi-Ghahnaviyeh, A; Boroushaki, M | Erfani, Arash; Rajabi-Ghahnaviyeh, Abbas; Boroushaki, Mehrdad | APR | 2018 | http://dx.doi.org/10.1016/j.buildenv.2018.02.022 | Model predictive control; Building energy saving; NARX modeling; Building management system; HVAC control; Multi-zone building | CO | Building and Environment | Traditional HVAC control strategies such as PID or PI controllers are inefficient due to the slow thermal dynamics of buildings. These systems often fail to optimize energy consumption effectively, especially in multi-zone AHUs. There's a lack of practical implementations combining non-linear modeling with predictive control in real systems. | 1. To design and implement a non-linear model predictive control (NMPC) system for a multi-zone AHU. 2. To reduce electricity and gas consumption while maintaining thermal comfort. | Subsystem | CAV system | Subsystem | Black-Box | Non-linear Autoregressive Network with Exogenous Inputs (NARX) | Some variables like return/discharge air flows are omitted due to sensor limitations | No | - | Yes | Real data | N/A | MATLAB | Real building | Multi-zone AHU serving 3 thermal zones in an educational building. | - | - | - | - | - | - | - | - | - | - | - | Communication: SIM900 GSM/GPRS module + web server; Hardware: thermometers, flow meters, ST32F microcontroller, custom PCB; Data Exchange: Web-based (HTTP communication between AHU and controller) | 17min | Zone damper positions, Chilled water flow rate, AHU status (on/off) | Low | Deviation from zone temperature set-points, Electricity consumption, Gas consumption | Pre-NMPC full operation baseline, On/off controller with fixed schedule | Yes | Full-scale real-world deployment | Yes | Model representation limit | ARTIFICIAL NEURAL-NETWORKS; ENERGY-CONSUMPTION; GENETIC ALGORITHMS; PUBLIC BUILDINGS; IDENTIFICATION; OPTIMIZATION; MANAGEMENT; COMFORT; MPC | [Erfani, Arash; Rajabi-Ghahnaviyeh, Abbas; Boroushaki, Mehrdad] Sharif Univ Technol, Dept Energy Engn, POB 14565-114,Azadi Ave, Tehran, Iran | Sharif University of Technology | Boroushaki, M (corresponding author), Sharif Univ Technol, Dept Energy Engn, POB 14565-114,Azadi Ave, Tehran, Iran. | boroushaki@sharif.edu | 16 | 20 | 133 |  |  |  | 237 | 245
112 | 112 | Adaptive-model predictive control of electronic expansion valves with adjustable setpoint for evaporator superheat minimization | Tesfay, M; Alsaleem, F; Arunasalam, P; Rao, A | Tesfay, Mehari; Alsaleem, Fadi; Arunasalam, Parthiban; Rao, Arvind | APR | 2018 | http://dx.doi.org/10.1016/j.buildenv.2018.02.015 | Setpoint algorithm; Adaptive-MPC; Expansion valves; Superheat | CO | Building and Environment | The literature lacks a control method for Electronic Expansion Valves (EEVs) that both handles the highly nonlinear HVAC dynamics and is practically implementable in real systems. Previous methods like PID, fuzzy, or non-adaptive MPC controllers do not dynamically adapt to varying operating conditions, which limits their performance in real-world HVAC scenarios. | The study proposes an Adaptive-Model Predictive Control (AMPC) framework that dynamically updates control parameters and setpoints to: 1. Minimize evaporator superheat. 2. Improve energy efficiency and system stability across varying load conditions. 3. Implement and validate this AMPC on real HVAC systems (1-ton and 2-ton systems). | Subsystem | HX | Component | Black-Box | First-order system with time delay + recursive least squares (RLS) for parameter identification. | Superheat response modeled as a first-order system with time delay. Assumes process dynamics can be approximated discretely with finite control and prediction horizons. | No | - | Yes | Real data | N/A | N/A | Real building | Carrier 1-ton unit: Single-speed compressor, outdoor installation; Midea 2-ton unit: Variable-speed compressor in a psychrometric chamber with controlled indoor/outdoor thermal conditions. | - | - | - | - | - | - | - | - | - | - | - | Universal SuperHeat Controller (USHC-G1.3b-BAAAXXX); Modular silicon expansion valve (MSEV-A12V-U112); Communication: MODBUS RTU and Windows GUI | 1s | Degree of opening of EEV | Low | Superheat stability, Energy efficiency (indirectly measured through COP), Controller responsiveness (rise time, overshoot) | Conventional PID controller, built-in manufacturer controller | Yes | Full-scale real-world deployment | Yes | Model representation limit | REFRIGERATION SYSTEM; OPERATIONAL STABILITY; FUNCTIONAL CONTROL | [Tesfay, Mehari; Alsaleem, Fadi] Univ Nebraska, Durham Sch Architectural Engn & Construct, Lincoln, NE 68588 USA; [Arunasalam, Parthiban; Rao, Arvind] DunAn Microstaq Inc, Austin, TX 78723 USA | University of Nebraska System; University of Nebraska Lincoln | Alsaleem, F (corresponding author), Univ Nebraska, Durham Sch Architectural Engn & Construct, Lincoln, NE 68588 USA. | mtesfay@unomaha.edu; falsaleem2@unl.edu; parthi@dmq-us.com; ARao@dmq-us.com | 24 | 26 | 133 |  |  |  | 151 | 160
113 | 113 | Quantifying demand flexibility of power-to-heat and thermal energy storage in the control of building heating systems | Finck, C; Li, RL; Kramer, R; Zeiler, W | Finck, Christian; Li, Rongling; Kramer, Rick; Zeiler, Wim | 2026-01-01 | 2018 | http://dx.doi.org/10.1016/j.apenergy.2017.11.036 | Thermal energy storage; Demand flexibility; Optimal control; Phase change material; Thermochemical material | EF | Applied Energy | The study addresses the need for quantifying and optimizing demand-side energy flexibility in buildings with integrated power-to-heat and thermal energy storage (TES) systems. Existing methods often overlook dynamic response, realistic storage modeling, and operational constraints in flexibility estimation. | 1. Develop detailed dynamic models for water, PCM, and TCM TES systems integrated with building heating systems. 2. Implement an optimal control framework (using dynamic programming) to assess and maximize demand flexibility. 3. Introduce new flexibility indicators, particularly the instantaneous power flexibility, to support grid services. | Subsystem | Building thermal, TES | Subsystem | White-Box | 1D convection-diffusion and enthalpy-based formulations (Crank–Nicolson scheme) for TES tanks; RC network model (via BRCM toolbox) for building thermal dynamics | 1D heat and mass transfer in TES tanks, No natural convection in PCM tank | Yes | Heat pump, Heat exchanger, Electric heater | No | None | BRCM Toolbox | MATLAB | Virtual testbed | Simulated two-story office building (135 m² per floor) equipped with a heat pump, electric heater, air-blown heat exchanger, and one of three TES types (water/PCM/TCM). Internal loads based on fixed occupancy schedule and weather from a TMY dataset (Netherlands, March 1). | Building thermal, TES | Subsystem | White-Box | 1D convection-diffusion and enthalpy-based formulations (Crank–Nicolson scheme) for TES tanks; RC network model (via BRCM toolbox) for building thermal dynamics | 1D heat and mass transfer in TES tanks, No natural convection in PCM tank | Yes | Heat pump, Heat exchanger, Electric heater | No | None | BRCM Toolbox | MATLAB | - | 15min | Charging/discharging schedule for TES, Heating power of heat pump and electric heater, Electricity consumption of heat pump and electric heater | Low | Total electricity cost, Indoor air temperature, Available storage capacity, Storage efficiency, Flexibility factor (cost-based), Power shifting capability, Instantaneous power flexibility | Basic feedback (P) controller, Comparison between three TES technologies under same conditions | No | Simulation only | No | The process model and testbed are the same | VARIABLE RENEWABLE POWER; MODEL-PREDICTIVE CONTROL; OF-THE-ART; SIDE MANAGEMENT; PCM; PUMPS; MASS; SOLIDIFICATION; OPTIMIZATION | [Finck, Christian; Kramer, Rick; Zeiler, Wim] Eindhoven Univ Technol, Dept Built Environm, Rondom 70, NL-5612 AP Eindhoven, Netherlands; [Li, Rongling] Tech Univ Denmark, Dept Civil Engn, Nils Koppels Alle Bldg 402, Lyngby 2800, Denmark | Eindhoven University of Technology; Technical University of Denmark | Finck, C (corresponding author), Eindhoven Univ Technol, Dept Built Environm, Rondom 70, NL-5612 AP Eindhoven, Netherlands. | c.j.finck@tue.nl | 181 | 184 | 209 |  |  |  | 409 | 425
114 | 114 | District heating and cooling systems - Framework for Modelica-based simulation and dynamic optimization | Schweiger, G; Larsson, PO; Magnusson, F; Lauenburg, P; Velut, S | Schweiger, Gerald; Larsson, Per-Ola; Magnusson, Fredrik; Lauenburg, Patrick; Velut, Stephane | 2026-10-15 | 2017 | http://dx.doi.org/10.1016/j.energy.2017.05.115 | District heating; District cooling; Smart energy systems; Modelica; Dynamic optimization; Dynamic simulation; Mixed-integer-optimal control | CO | Energy | Most existing optimization tools for district heating systems rely on heavily simplified static or algebraic models, and cannot adequately represent dynamic behaviors such as thermal inertia, mass flow-dependent delays, or realistic heat propagation. There is also a lack of frameworks that integrate simulation and optimization in a scalable, real-time capable way. | The paper aims to develop and demonstrate a Modelica-based framework that supports both dynamic thermo-hydraulic simulation and mixed-integer optimal control (MINLP) optimization of large-scale 4th Generation District Heating (4GDH) systems. It proposes a novel decomposition method for solving MINLP problems efficiently and tests this approach via simulation-based use cases. | Subsystem | DHC | Subsystem | White-Box | The continuous-time DAEs are converted into an NLP (Nonlinear Program) (discretized via direct collocation) | Plug-flow + mixed volume approach for heat transport, Quasi-steady pressure drops | No | - | Yes | Validated platform | Optimica Compiler Toolkit, CasADI, IPOPT, Pyomo, Gurobi | Modelica, Python | Virtual testbed | 1. Large-scale virtual district heating system with 103 consumers and 14,000m of piping (used for simulation-only scale testing); 2. Virtual city district with 16 consumers, 4200m of piping (used for continuous optimization and validation) | DHC | Subsystem | White-Box | 1D energy balance for pipes (PDE), plug-flow models, simplified consumer/producer models | Plug-flow + mixed volume approach for heat transport, Quasi-steady pressure drops | No | - | Yes | Validated platform | N/A | Modelica | - | 864s | Producer supply temperature, Producer pressure, Heat output scheduling (on/off status and thermal output) | Low, Medium | Supply temperature minimization, Constraint satisfaction (temperature, pressure, flow), Real-time feasibility | None | No | Simulation only | No | The process model and testbed are the same | ENERGY-SYSTEMS; RENEWABLE ENERGY; OPERATION; INTEGRATION; NETWORKS; STORAGE | [Schweiger, Gerald] AEE Inst Sustainable Technol, A-8200 Gleisdorf, Austria; [Larsson, Per-Ola; Magnusson, Fredrik; Velut, Stephane] Modelon AB, SE-22370 Lund, Sweden; [Lauenburg, Patrick] Lund Univ, Dept Energy Sci, SE-22100 Lund, Sweden | Lund University | Schweiger, G (corresponding author), AEE Inst Sustainable Technol, A-8200 Gleisdorf, Austria. | g.schweiger@aee.at | 99 | 103 | 137 |  |  |  | 566 | 578
115 | 115 | Dynamic programming and genetic algorithms to control an HVAC system: Maximizing thermal comfort and minimizing cost with PV production and storage | Pombeiro, H; Machado, MJ; Silva, C | Pombeiro, Henrique; Machado, Maria Joao; Silva, Carlos | OCT | 2017 | http://dx.doi.org/10.1016/j.scs.2017.05.021 | Energy efficiency; Optimization; Thermal comfort; PV production; Storage; Demand response; Genetic algorithm; Dynamic programming | EF | Sustainable Cities and Society | The study identifies a need for intelligent HVAC control systems that optimize both thermal comfort and energy cost, especially in the context of integrating photovoltaic (PV) energy and battery storage. Existing Building Energy Management Systems (BEMS) often lack robust integration of building energy data into actionable control strategies. | 1. Develop and compare three HVAC control strategies: - Dynamic Programming (DP) with a Simplified Thermal Model (STM), - Genetic Algorithm (GA) with STM, - GA with EnergyPlus (EP) simulation model; 2. Test the models in a real experimental environment. 3. Optimize both user comfort and operational costs, considering dynamic tariffs and on-site PV generation with storage. | Subsystem | Building thermal | Component | Gray-Box, White-Box | STM: Transient energy balance equations; EP: Detailed physical modeling with EnergyPlus | STM neglects thermal inertia; EP includes detailed occupancy schedules, HVAC parameters, and weather forecasts | No | - | Yes | Real data | N/A | MATLAB, EnergyPlus | Lab | Experimental room in IST, TagusPark, Lisbon; Equipped with sensors (temperature, RH, luminosity), PV panels, and a fan coil HVAC | - | - | - | - | - | - | - | - | - | - | - | Sensors: Berker 75900056 (Temp, RH, Lux); Data acquisition: Weather station & Meteo IST forecast platform | STM-based: 1h; EP-based: 10min | Fan coil speed (0–3); Source of electricity (grid vs. battery) | Low | Thermal comfort; Cost (monetary expenditure); PV electricity utilization | Comparison across three models: DP+STM, GA+STM, GA+EP | Partial | Lab setup | Yes | Model representation limit | ZERO-ENERGY BUILDINGS; DEMAND RESPONSE; MANAGEMENT; OPTIMIZATION; CONSUMPTION; AUTOMATION; BEHAVIOR; DESIGN | [Pombeiro, Henrique; Machado, Maria Joao; Silva, Carlos] Univ Lisbon, Inst Super Tecn, Lisbon, Portugal; [Pombeiro, Henrique; Silva, Carlos] Ctr Innovat Technol & Policy Res, IN, Lisbon, Portugal | Universidade de Lisboa; Universidade de Lisboa | Pombeiro, H (corresponding author), Univ Lisbon, Inst Super Tecn, Lisbon, Portugal. | henrique.pombeiro@tecnico.ulisboa.pt; maria.joao.machado@tecnico.ulisboa.pt; carlos.santos.silva@tecnico.ulisboa.pt | 46 | 48 | 34 |  |  |  | 228 | 238
116 | 116 | Building-to-grid predictive power flow control for demand response and demand flexibility programs | Razmara, M; Bharati, GR; Hanover, D; Shahbakhti, M; Paudyal, S; Robinett, RD | Razmara, M.; Bharati, G. R.; Hanover, Drew; Shahbakhti, M.; Paudyal, S.; Robinett, R. D., III | 2026-10-01 | 2017 | http://dx.doi.org/10.1016/j.apenergy.2017.06.040 | Demand response; Demand flexibility; Building to Grid (B2G); Building predictive control; Solar PV panel integration; Energy storage system integration; Monte-Carlo simulation | EF | Applied Energy | Traditional demand response (DR) methods do not fully utilize building-side flexibility or offer predictive coordination with grid constraints, especially in the presence of distributed energy resources like PV and batteries. There is also a lack of unified predictive control frameworks that simultaneously optimize supply and demand across building-to-grid (B2G) systems. | 1. Develop a unified Model Predictive Control (MPC) framework to coordinate building HVAC systems, battery energy storage, and PV generation for DR and energy flexibility. 2. Reduce building electricity cost and grid ramp-rates. 3. Integrate deterministic and probabilistic modeling to assess uncertainty impacts. | Subsystem | Building thermal, BES | Component | Gray-Box | RC network for thermal dynamics; Equivalent circuit for battery (manufacturer-based map) | Linear building RC thermal model; Known battery voltage, temperature, and performance maps | Yes | PV panel, Distribution grid | Yes | Real data | YALMIP | MATLAB | Virtual testbed | 1. Real: 3-story, 61,500 ft² office building (Lakeshore Center at Michigan Technological University), Equipped with Ground Source Heat Pumps (GSHPs) with COP of 3.2, Temperature sensors in each zone with 1-minute resolution, Historical building load data used, Integrated with solar PV, battery storage, and 3-phase distribution grid; 2. Virtual: Modified IEEE 13-node feeder with 27 buildings. | Building thermal, BES | Component | Gray-Box | RC network for thermal dynamics; Equivalent circuit for battery (manufacturer-based map) | Linear building RC thermal model; Known battery voltage, temperature, and performance maps | Yes | PV panel, Distribution grid | Yes | Real data | N/A | MATLAB | - | 30min | Supply air temperature, Battery charge/discharge power | Medium | Electricity cost savings, Load ramp-rate reduction, Comfort constraint violations (tracked via slack variables), Voltage constraint satisfaction in grid | Rule-Based Controller (RBC), Unidirectional vs. bidirectional MPC, Topology I (PV-only charge) vs. Topology II (PV + grid charge) | No | Simulation only | No | The process model and testbed are the same | RULE-BASED CONTROL; MODEL | [Razmara, M.; Hanover, Drew; Shahbakhti, M.; Robinett, R. D., III] Michigan Technol Univ, Mech Engn Engn Mech, Houghton, MI 49931 USA; [Bharati, G. R.; Paudyal, S.] Michigan Technol Univ, Dept Elect & Comp Engn, Houghton, MI 49931 USA | Michigan Technological University; Michigan Technological University | Razmara, M (corresponding author), Michigan Technol Univ, Mech Engn Engn Mech, Houghton, MI 49931 USA. | mrazmara@mtu.edu; grbharati@mtu.edu; djhanove@mtu.edu; mahdish@mtu.edu; sumitp@mtu.edu | 102 | 109 | 203 |  |  |  | 128 | 141
117 | 117 | Experimental demonstration of buildings providing frequency regulation services in the Swiss market | Gorecki, TT; Fabietti, L; Qureshi, FA; Jones, CN | Gorecki, Tomasz T.; Fabietti, Luca; Qureshi, Faran A.; Jones, Colin N. | 2026-06-01 | 2017 | http://dx.doi.org/10.1016/j.enbuild.2017.02.050 | Ancillary services; Demand response; Building control; MPC; Frequency control; Power flexibility | EF | Energy and Buildings | Traditional ancillary services in power grids rely on supply-side flexibility. The potential for demand-side resources (like buildings) to offer frequency regulation remains under-explored, particularly in real-world settings that comply with strict market rules such as in Switzerland. Prior works often ignore regulatory constraints or only simulate performance with fixed baselines. | 1. Develop a model-based strategy to enable commercial buildings to participate in secondary frequency regulation in compliance with Swiss market rules. 2. Introduce a hierarchical control scheme that includes intraday energy market participation. 3. Demonstrate effectiveness and robustness of the method through real-world experiments in occupied office spaces. | Subsystem | Indoor air temperature | Component | Black-Box | ARX (AutoRegressive with eXogenous inputs) identified via least squares. | Linear time-invariant dynamics | No | - | Yes | Real data | YALMIP | MATLAB | Real building, Virtual testbed | Five-zone office building (115 m²) with electric resistance heaters (1900 W each); Occupied during experiments; Real-time control via BeagleBone Black and Ethernet-connected server; Zones have different sun exposures and heating demands | Indoor air temperature | Component | Black-Box | ARX (AutoRegressive with eXogenous inputs) identified via least squares. | Linear time-invariant dynamics | No | - | Yes | Real data | N/A | MATLAB | Wireless temperature sensor, Micro-computers (BeagleBone Black) | Reserve scheduler: daily; MPC: every 15 minutes; Tracking controller: every 1 second | Level 1 reserve scheduler: reserve capacity (γ) and baseline power schedule, plus the affine policy parameters; Level 2: Sets heating power / PWM set-points; Level 3: Heater power levels via PWM (0–1 scale) | Low, Medium, High | Regulation capacity offered (% of total installed power); Thermal comfort; Constraint violation; Intraday trade volume and cost | Control strategy without intraday trading | Yes | Full-scale real-world deployment | Yes, No | Real: Model representation limit; (Virtual: The process model and testbed are the same) | HVAC CHILLER CONTROL | [Gorecki, Tomasz T.; Fabietti, Luca; Qureshi, Faran A.; Jones, Colin N.] Ecole Polytech Fed Lausanne, Automat Control Lab, Lausanne, Switzerland | Swiss Federal Institutes of Technology Domain; Ecole Polytechnique Federale de Lausanne | Gorecki, TT (corresponding author), Ecole Polytech Fed Lausanne, Automat Control Lab, Lausanne, Switzerland. | tomasz.gorecki@epfl.ch; luca.fabietti@epfl.ch; faran.qureshi@epfl.ch; colin.jones@epfl.ch | 23 | 25 | 144 |  |  |  | 229 | 240
118 | 118 | Temperature and humidity adaptive control in multi-enclosed thermal zones under unexpected external disturbances | Buonomano, A; Montanaro, U; Palombo, A; Santini, S | Buonomano, Annamaria; Montanaro, Umberto; Palombo, Adolfo; Santini, Stefania | 2026-01-15 | 2017 | http://dx.doi.org/10.1016/j.enbuild.2016.11.015 | Building simulation; Model reference adaptive control algorithm; Multi enclosed zones; Thermo hygrometric analysis | CO | Energy and Buildings | Existing HVAC control strategies (e.g., PID) are insufficient for maintaining strict and stable temperature/humidity in multi-enclosed zones subject to rapid and unknown disturbances, especially in sensitive environments like museums and NICUs. Moreover, most prior studies either neglected zone interactions or used oversimplified models. | 1. Develop a new adaptive control strategy (LQ-EMRAC) for regulating temperature and humidity in multi-enclosed thermal zones. 2. Integrate this into a flexible dynamic simulation platform (DETECt 2.3.1). 3. Evaluate robustness under varying weather, occupancy, and disturbance scenarios through virtual testbeds simulating museum and hospital settings. | Subsystem | Indoor air temperature, IAQ | Component | White-Box | Reduced-order linear time-invariant form with unknown disturbance term | Fully mixed air in each zone, Lumped thermal and moisture capacities, 1D transient heat transfer, Enclosed zones modeled as lumped envelopes | No | - | No | None | N/A | MATLAB | Virtual testbed | Two case studies modeled as virtual testbeds: Museum: Zone 1 = hall (intermittent HVAC), Zone 2 = glass display case (continuous HVAC, strict 20°C/65%RH); Hospital NICU: Zone 1 = ward; Zones 2–7 = six incubators with different setpoints based on infant condition (29–34°C, 40–85%RH) | Indoor air temperature, IAQ | Component | White-Box | RC thermal + moisture mass balance | Lumped modeling, fully mixed zones, no detailed HVAC equipment models | No | - | No | None | N/A | MATLAB | - | 10 min (display case), 50 min (museum hall) | Sensible and latent energy inputs | Medium | Temperature and RH tracking error, Peak loads, Energy demands, Comfort indices | Baseline performance without adaptive control | No | Simulation only | Yes | Model representation limit | ENERGY PERFORMANCE ANALYSIS; DYNAMIC SIMULATION CODE; MUSEUM CLIMATE CLASSES; INFANT-INCUBATOR; INDOOR CLIMATE; INTEGRAL MRAC; MODEL; ENVIRONMENT; SYSTEMS; IMPACT | [Buonomano, Annamaria; Montanaro, Umberto; Palombo, Adolfo] Univ Naples Federico II, Dept Ind Engn, Naples, Italy; [Santini, Stefania] Univ Naples Federico II, Dept Elect Engn & Informat Technol, Naples, Italy | University of Naples Federico II; University of Naples Federico II | Montanaro, U (corresponding author), Univ Naples Federico II, Dept Ind Engn, Naples, Italy. | umberto.montanaro@unina.it | 41 | 42 | 135 |  |  |  | 263 | 285
119 | 119 | Transactive Control of Commercial Buildings for Demand Response | Hao, H; Corbin, CD; Kalsi, K; Pratt, RG | Hao, He; Corbin, Charles D.; Kalsi, Karanjit; Pratt, Robert G. | JAN | 2017 | http://dx.doi.org/10.1109/TPWRS.2016.2559485 | Commercial buildings; demand response; HVAC systems; market mechanism; transactive control | EF | IEEE Transactions on Power Systems | Existing demand response (DR) strategies for commercial buildings often lack reliability, privacy preservation, and fine-grained control coordination. Prior works either rely on simple price-response strategies (unpredictable) or direct load control (intrusive). Additionally, most market-based control studies target residential HVAC with simplified dynamics, not complex commercial systems. | 1. Propose a novel transactive control strategy for commercial HVAC systems using a distributed market-based approach. 2. Develop a multi-agent double-auction market mechanism to coordinate HVAC subsystems. 3. Use simplified physical models to derive demand bids while ensuring comfort and operational feasibility. 4. Demonstrate effectiveness through simulations using EnergyPlus-based virtual testbed. | Whole System | Indoor air temperature | Component | Gray-Box | Linearized RC-like model | Linear zone thermal dynamics | Yes | Chiller and fan power | Yes | Real data | N/A | Python | Virtual testbed | Co-simulation testbed combining EnergyPlus, BCVTB, and Python agents; based on a real SEB building with 17 zones served by one AHU. | Building thermal | Component | White-Box | Physics-based modeling using EnergyPlus | Standard EnergyPlus modeling | Yes | Chiller and fan power | Yes | Real data | BCVTB | Python, EnergyPlus | - | 5min | Zone temperature setpoints | High | Peak load reduction, Energy consumption savings, Zone temperature deviation | Baseline with fixed 21 °C setpoints | No | Simulation only | Yes | Model representation limit | ANCILLARY SERVICE; COOLING COILS; ENERGY; OPTIMIZATION; EQUILIBRIUM; FLEXIBILITY | [Hao, He; Corbin, Charles D.; Kalsi, Karanjit; Pratt, Robert G.] Pacific Northwest Natl Lab, Elect Infrastruct & Bldg Div, Richland, WA 99354 USA | United States Department of Energy (DOE); Pacific Northwest National Laboratory | Hao, H (corresponding author), Pacific Northwest Natl Lab, Elect Infrastruct & Bldg Div, Richland, WA 99354 USA. | He.Hao@pnnl.gov; Charles.Corbin@pnnl.gov; Karanjit.Kalsi@pnnl.gov; Robert.Pratt@pnnl.gov | 203 | 232 | 32 | 1 |  |  | 774 | 783
120 | 120 | Energy-efficiency-oriented cascade control for vapor compression refrigeration cycle systems | Yin, XH; Wang, XL; Li, SY; Cai, WJ | Yin, Xiaohong; Wang, Xinli; Li, Shaoyuan; Cai, Wenjian | 2026-12-01 | 2016 | http://dx.doi.org/10.1016/j.energy.2016.10.059 | Vapor compression refrigeration cycle; Superheat; Model predictive control; Cascade control | CO | Energy | Traditional PID-based control strategies in HVAC vapor compression cycle (VCC) systems do not adequately balance energy efficiency with meeting cooling demand. These strategies often maintain a constant superheat degree, which may lead to inefficient energy usage or unstable operation, especially under varying cooling demands. | The paper proposes an energy-efficiency-oriented cascade control strategy using a combination of PI and MPC. The outer loop calculates an optimal superheat setting based on cooling demand, while the inner loop employs MPC to control evaporator superheat and pressure difference, aiming to: Enhance energy efficiency; Meet variable cooling loads robustly; Maintain safe compressor operation. | Subsystem | VCS | Subsystem | Black-Box | N4SID (Numerical Algorithm for Subspace State Space System ID) for linear state-space modeling. | 1. Superheat region has constant refrigerant density. 2. Evaporator is divided into superheat and two-phase regions. 3. Certain thermodynamic relationships (enthalpy, saturation temperature) are curve-fitted. 4. Ambient temperature is the only external disturbance considered. | No | - | Yes | Lab | N/A | N/A | Lab | Refrigeration test platform at Nanyang Technological University, Singapore. Includes: Variable-speed compressor (HG22P); Air-cooled evaporator and condenser; Three electronic expansion valves; Nominal capacity: 5.0 kW; Full instrumentation with temperature/pressure sensors and flow meters | - | - | - | - | - | - | - | - | - | - | - | Sensors (temperature, pressure); Flowmeter | Outer loop: 60 s; Inner loop: 10 s | Compressor speed; Expansion valve opening | Low | Energy efficiency (via COP); Tracking accuracy (RMS of superheat deviation); Stability (overshoot, settling time) | PI–MPC (proposed); MPC–MPC; PI–PID; MPC–PID | Partial | Lab setup | Yes | Model representation limit | MODEL-PREDICTIVE CONTROL; AIR-CONDITIONING SYSTEMS; TEMPERATURE CONTROL; OPTIMIZATION | [Yin, Xiaohong] Qingdao Univ Sci & Technol, Sch Automat & Elect Engn, Qingdao 266042, Peoples R China; [Wang, Xinli] Shandong Univ, Sch Control Sci & Engn, Jinan 250061, Peoples R China; [Li, Shaoyuan] Shanghai Jiao Tong Univ, Dept Automat, Key Lab Syst Control & Informat Proc, Minist Educcit China, Shanghai 200240, Peoples R China; [Cai, Wenjian] Nanyang Technol Univ, Sch Elect & Elect Engn, Ctr E City, EXQUISITUS, Singapore 639798, Singapore | Qingdao University of Science & Technology; Shandong University; Shanghai Jiao Tong University; Nanyang Technological University | Wang, XL (corresponding author), Shandong Univ, Sch Control Sci & Engn, Jinan 250061, Peoples R China. | xlwangzju@163.com | 31 | 32 | 116 |  | 1 |  | 1006 | 1019
121 | 121 | Robust Energy-Constrained Frequency Reserves From Aggregations of Commercial Buildings | Vrettos, E; Oldewurtel, F; Andersson, G | Vrettos, Evangelos; Oldewurtel, Frauke; Andersson, Goran | NOV | 2016 | http://dx.doi.org/10.1109/TPWRS.2015.2511541 | Ancillary services; demand response; energy constraints; frequency control; robust model predictive control | EF | IEEE Transactions on Power Systems | The paper addresses the lack of reliable, scalable frameworks for leveraging commercial buildings’ HVAC systems to provide secondary frequency control (SFC) reserves. It especially focuses on the challenge of dealing with energy-constrained frequency signals and ensuring robustness despite uncertain reserve activation signals and physical system limitations. | 1. Develop a three-level hierarchical control framework for reserve scheduling and provision by HVAC systems in building aggregations. 2. Incorporate energy-constrained frequency signals and model their uncertainty. 3. Estimate the reserve potential of building aggregations under varying product characteristics using simulation studies. | Subsystem | Building thermal | Component | Gray-Box | 12th-order RC model (multi-input, multi-output) | Bilinearities eliminated via disturbance fixing and sequential linear programming | Yes | Power consumption of HP | Yes | Simulated data | N/A | N/A | Virtual testbed | Aggregation of six large Swiss office buildings (15,000 m² each), different HVAC system types (radiators + chilled ceilings vs. TABS) | Building thermal | Component | Gray-Box | Same RC model used | Bilinearities eliminated via disturbance fixing and sequential linear programming | Yes | Power consumption of HP | Yes | Simulated data | N/A | N/A | - | Reserve scheduling (Lv1): once per day; HVAC MPC (Lv2): every 30 minutes; Reserve tracking (Lv3): every 10 seconds | Level 1 – Aggregator Scheduling: Reserve capacity of building, Baseline electrical-power trajectory, Affine recourse policy; Level 2– Building-Level Robust MPC: HVAC set-points (power or supply-temperature targets); Level 3– Fast Frequency-Tracking Controller: Real-time electrical-power command (Implemented via refrigerant-valve modulation or inverter frequency so total building power tracks the command) | Low, Medium, High | Reserve capacity; HVAC energy consumption; Comfort zone maintenance (temperature limits); Total cost = electricity cost - reserve profit | Energy-optimal control (MPC without reserve provision) | No | Simulation only | No | The process model and testbed are the same | HVAC SYSTEMS; DEMAND RESPONSE; MODEL; OPTIMIZATION; LOADS; POWER | [Vrettos, Evangelos; Andersson, Goran] Swiss Fed Inst Technol, EEH Power Syst Lab, CH-8092 Zurich, Switzerland; [Oldewurtel, Frauke] Univ Calif Berkeley, Dept Elect Engn & Comp Sci, Berkeley, CA 94720 USA | Swiss Federal Institutes of Technology Domain; ETH Zurich; University of California System; University of California Berkeley | Vrettos, E (corresponding author), Swiss Fed Inst Technol, EEH Power Syst Lab, CH-8092 Zurich, Switzerland. | vrettos@eeh.ee.ethz.ch; old-ewurtel@berkeley.edu; andersson@eeh.ee.ethz.ch | 77 | 82 | 31 | 6 |  |  | 4272 | 4285
122 | 122 | Bridging the gap between the linear and nonlinear predictive control: Adaptations for efficient building climate control | Pcolka, M; Záceková, E; Robinett, R; Celikovsky, S; Sebek, M | Pcolka, Matej; Zacekova, Eva; Robinett, Rush; Celikovsky, Sergej; Sebek, Michael | AUG | 2016 | http://dx.doi.org/10.1016/j.conengprac.2016.01.007 | Model predictive control; Identification for control; Building climate control | CO | Control Engineering Practice | 1. Linear MPC (Model Predictive Control) is efficient but relies on simplified models and cannot optimize nonlinear criteria. 2. Nonlinear MPC offers better fidelity but is computationally expensive and less practical for real buildings. 3. Real-life building systems often include discrete actuator constraints not handled well in standard MPC. | 1. Propose a linear time-dependent predictive controller to bridge the gap between linear and nonlinear MPC. 2. Develop new identification methods (MRI) for both linear and nonlinear models for improved prediction. 3. Adapt MPC algorithms to handle discrete-valued actuators (e.g., quantized water mass flow rates). 4. Compare linear, nonlinear, and linear time-varying MPCs using a high-fidelity TRNSYS building simulation. | Subsystem | Building thermal | Component | White-Box | Nonlinear: Thermodynamic differential equations derived from first principles (convection, conduction, radiation, ambient effects); Linear: Linearized state-space model with identified parameters; Time-varying linear: Switched linear approximations based on auxiliary state differences | Constant thermal properties across prediction intervals; Simplifications for heat transfer dynamics (e.g., approximated radiation) | No | - | Yes | Simulated data | N/A | MATLAB | Virtual testbed | One-zone, medium-weight building (5 × 5 × 3 m³), single-glazed window; TABS system; environmental inputs based on Prague weather profile via TRNSYS Type 15 | Building thermal | Component | White-Box | Physics-based TRNSYS simulation model | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | 15min | Supply water temperature, Mass flow rate | Medium | Thermal comfort violation (defined as temperature below threshold), Energy cost (hot water, electricity) | Linear MPC with LM, Linear MPC with SLM | No | Simulation only | Yes | Model representation limit | RELEVANT IDENTIFICATION; MPC; MODEL | [Pcolka, Matej; Zacekova, Eva; Sebek, Michael] Czech Tech Univ, Fac Elect Engn, Dept Control Engn, Tech 2, Prague 16627 6, Czech Republic; [Robinett, Rush] Michigan Technol Univ, Mech Engn Engn Mech, Houghton, MI 49931 USA; [Celikovsky, Sergej] Acad Sci Czech Republ, Inst Informat Theory & Automat, Prague, Czech Republic | Czech Technical University Prague; Michigan Technological University; Czech Academy of Sciences; Institute of Information Theory & Automation of the Czech Academy of Sciences | Pcolka, M; Záceková, E (corresponding author), Czech Tech Univ, Fac Elect Engn, Dept Control Engn, Tech 2, Prague 16627 6, Czech Republic. | matej.pcolka@fel.cvut.cz; eva.zacekova@fel.cvut.cz; rdrobine@mtu.edu; celikovs@utia.cas.cz; sebekm1@fel.cvut.cz | 15 | 17 | 53 |  |  | SI | 124 | 138
123 | 123 | Demand-response in building heating systems: A Model Predictive Control approach | Bianchini, G; Casini, M; Vicino, A; Zarrilli, D | Bianchini, Gianni; Casini, Marco; Vicino, Antonio; Zarrilli, Donato | 2026-04-15 | 2016 | http://dx.doi.org/10.1016/j.apenergy.2016.01.088 | Energy management systems; Model Predictive Control; Building heating systems; Demand response; Mathematical modeling; Optimization | EF | Applied Energy | Traditional rule-based HVAC control strategies in buildings are outdated and inefficient. Although MPC has been applied to building control, its application to demand response (DR) scenarios involving price–volume signals and large-scale buildings remains computationally intractable due to MILP complexity. | 1. Develop a cost-optimal MPC-based control strategy that enables participation in DR programs using price–volume signals. 2. Ensure computational feasibility for large-scale buildings by introducing a decoupled heuristic control approach. 3. Validate the proposed method using realistic simulation environments (EnergyPlus). | Subsystem | Indoor air temperature | Component | Black-Box | Linear AutoRegressive model with eXogenous inputs (ARX) | Zones are thermally decoupled (no inter-zone heat transfer). | No | - | Yes | Simulated data | System Identification Toolbox | MATLAB | Virtual testbed | Two cases: 1. Three-zone office in Milan with radiant floors; 2. 100-zone, 5-floor building with fan coils. Both testbeds are simulated in EnergyPlus and modeled via DesignBuilder for large-scale case. | Building thermal | Component | White-Box | Physical building simulation via EnergyPlus | Standard EnergyPlus modeling | No | - | Yes | Validated platform | N/A | EnergyPlus | - | 10min | Heater status (on/off) | Low | Energy cost minimization; Demand response reward earnings; Comfort constraints satisfaction; Computation time | Optimal MPC (coupled MILP); Relaxed optimal control with continuous control signals (for large case) | No | Simulation only | Yes | Model representation limit | PRICE | [Bianchini, Gianni; Casini, Marco; Vicino, Antonio; Zarrilli, Donato] Univ Siena, Dipartimento Ingn Informaz & Sci Matemat, Via Roma 56, I-53100 Siena, Italy | University of Siena | Bianchini, G (corresponding author), Univ Siena, Dipartimento Ingn Informaz & Sci Matemat, Via Roma 56, I-53100 Siena, Italy. | giannibi@diism.unisi.it; casini@diism.unisi.it; vicino@diism.unisi.it; zarrilli@diism.unisi.it | 134 | 142 | 168 |  |  |  | 159 | 170
124 | 124 | Scheduling and Provision of Secondary Frequency Reserves by Aggregations of Commercial Buildings | Vrettos, E; Andersson, G | Vrettos, Evangelos; Andersson, Goeran | APR | 2016 | http://dx.doi.org/10.1109/TSTE.2015.2497407 | Ancillary services; frequency control; demand response; commercial buildings; robust and stochastic optimization; chance-constraints; model predictive control | EF | IEEE Transactions on Sustainable Energy | Most previous studies focused on building-level reserve provision or assumed ideal SFC signals. Limited attention has been paid to integrating energy-constrained SFC signals, chance-constrained comfort zones, and detailed HVAC dynamics within an aggregated commercial building framework. | 1. Extend previous robust control frameworks for secondary frequency control (SFC) to allow for energy-constrained SFC signals and asymmetric reserves. 2. Incorporate HVAC model predictive control (MPC) and reserve scheduling with chance constraints. 3. Develop and integrate realistic dynamic models of heat pump (HP) systems into the reserve provision framework. 4. Evaluate tracking quality and reserve capacity via simulation of a Swiss building aggregation. | Subsystem | Indoor air temperature, HP | Subsystem | Gray-Box | Thermal Dynamics: 12th-order bilinear RC model linearized to a time-varying linear model; Heat Pump Dynamics: Nonlinear system with linear approximations for use in optimization and dynamics modeled via second-order overdamped system with dead time and delay components. | Time-scale separation between thermal envelope (slow) and HP dynamics (fast) | No | - | Yes | Simulated data | CPLEX, YALMIP | MATLAB | Virtual testbed | Aggregation of 6 typical Swiss office buildings (15,000 m² each), with different HVAC systems (radiators + cooled ceilings or TABS), construction types, and window-to-wall ratios. | Indoor air temperature, HP | Subsystem | Gray-Box | Thermal Dynamics: 12th-order bilinear RC model linearized to a time-varying linear model; Heat Pump Dynamics: Nonlinear system with linear approximations for use in optimization and dynamics modeled via second-order overdamped system with dead time and delay components. | Time-scale separation between thermal envelope (slow) and HP dynamics (fast) | No | - | Yes | Simulated data | N/A | MATLAB | - | Reserve scheduling: 1 day; HVAC MPC: 15 min – 1 hour; HP tracking: seconds | Level 1 — Reserve scheduling: Reserve capacities, Affine feedback policy; Level 2 — Building climate control: HP thermal power setpoint; L3 – Fast tracking: HP/chiller electric-power (via refrigerant-flow control) | Low, Medium, High | SFC signal tracking MAPE, Electricity cost, Reserve capacity offered, Comfort zone violation probability, Computation time | Fully robust approaches (RPC, RPEC), No reserve provision, Open-loop vs. closed-loop optimization, Different chance constraint thresholds | No | Simulation only | No | The process model and testbed are the same | MODEL-PREDICTIVE CONTROL; ANCILLARY SERVICES; DEMAND RESPONSE | [Vrettos, Evangelos; Andersson, Goeran] Swiss Fed Inst Technol, EEH Power Syst Lab, CH-8092 Zurich, Switzerland | Swiss Federal Institutes of Technology Domain; ETH Zurich | Vrettos, E; Andersson, G (corresponding author), Swiss Fed Inst Technol, EEH Power Syst Lab, CH-8092 Zurich, Switzerland. | vrettos@eeh.ee.ethz.ch; andersson@eeh.ee.ethz.ch | 61 | 77 | 7 | 2 |  |  | 850 | 864
125 | 125 | Optimal Control Approaches for Analysis of Energy Use Minimization of Hybrid Ground-Coupled Heat Pump Systems | Atam, E; Patteeuw, D; Antonov, SP; Helsen, L | Atam, Ercan; Patteeuw, Dieter; Antonov, Stefan P.; Helsen, Lieve | MAR | 2016 | http://dx.doi.org/10.1109/TCST.2015.2445851 | Borefield; dynamic programming (DP); hybrid ground-coupled heat pumps; nonlinear model predictive control (NMPC); optimal control | CO | IEEE Transactions on Control Systems Technology | The paper addresses the lack of realistic, high-fidelity control-oriented models and intelligent control strategies for hybrid ground-coupled heat pump (HyGCHP) systems. Previous works either relied on simplistic models or used rule-based control strategies that poorly capture physical constraints like borehole temperature limits, leading to suboptimal performance. | 1. To develop and evaluate three control strategies—Dynamic Programming (DP), Nonlinear Model Predictive Control (NMPC), and Linear Optimal Control (LOC)—for minimizing energy use in HyGCHP systems. 2. To compare these controllers under different building load profiles and operational constraints. 3. To assess the realism of controller design by employing data-driven and reduced-order models validated against a detailed emulator. | Subsystem | Borehole heat exchanger | Component | Black-Box, Gray-Box | NARX neural network model (black-box) for DP; Proper Orthogonal Decomposition (POD)-based reduced-order model (SS-ROM) for NMPC | NARX is trained on emulator output and uses 4-hour sampling. SS-ROM is derived from a large-scale finite-volume heat conduction model. | No | - | Yes | Simulated data | System Identification Toolbox, Optimization Toolbox | MATLAB | Virtual testbed | A large-scale finite-volume emulator model simulating an equivalent borehole with grout and soil zones. 1D radial heat conduction model, 506 states, 1-second sampling. | Borehole heat exchanger | Component | White-Box | Finite-volume numerical model using equivalent-diameter method | Single borehole approximation, neglects borehole interactions | No | - | No | None | Simulink | MATLAB | - | 4h | Heating: Thermal power of heat pump and gas boiler; Cooling: Thermal power of passive cooler and chiller | Medium | Annual energy cost, thermal build-up/depletion (TBUD), temperature violation, computation time | DP is used as the global optimal reference. NMPC and LOC are compared against DP under identical constraints. | No | Simulation only | Yes | Model representation limit |  | [Atam, Ercan; Patteeuw, Dieter; Antonov, Stefan P.; Helsen, Lieve] Katholieke Univ Leuven, Dept Mech Engn, B-3001 Leuven, Belgium; [Helsen, Lieve] EnergyVille, B-3600 Genk, Belgium | KU Leuven | Atam, E; Patteeuw, D; Antonov, SP; Helsen, L (corresponding author), Katholieke Univ Leuven, Dept Mech Engn, B-3001 Leuven, Belgium. | ercan.atam@kuleuven.be; dieter.patteeuw@kuleuven.be; stefan.antonov@kuleuven.be; lieve.helsen@kuleuven.be | 37 | 37 | 24 | 2 |  |  | 525 | 540
126 | 126 | Cooperative fuzzy model predictive control for heating and cooling of buildings | Killian, M; Mayer, B; Kozek, M | Killian, M.; Mayer, B.; Kozek, M. | 2026-01-15 | 2016 | http://dx.doi.org/10.1016/j.enbuild.2015.12.017 | Grey-box modelling; Fuzzy MPC; Cooperative FMPC; Building control | CO | Energy and Buildings | Existing control strategies for buildings either focus on heating or cooling alone, lack coordination across zones, or cannot handle the nonlinear and seasonal dynamics of building behavior. There’s a need for an intelligent, flexible control strategy that accommodates multiple zones, different time constants (fast and slow dynamics), and seasonal changes. | 1. Propose a Cooperative Fuzzy Model Predictive Control (CFMPC) for heating and cooling. 2. Develop nonlinear grey-box models using local linear models (LLMs) for different seasons. 3. Coordinate fuzzy MPCs across zones with a cooperative iteration-loop. 4. Compare CFMPC performance against linear MPC, non-cooperative FMPC, and a rule-based PID. | Subsystem | Indoor air temperature | Component | Gray-Box | Local Linear Model Networks (LLMNs) via LoLiMoT algorithm; ARX-based models embedded in TS-fuzzy framework | Seasonal dynamics segmented into three regimes (winter, summer, transition); Ambient temperature is the partitioning variable; Constant mass flow and specific heat capacity | No | - | Yes | Real data | N/A | N/A | Virtual testbed | A simulated version of a 27,000 m² university building in Salzburg, Austria, divided into 4 zones (NE, SE, SW, NW), each fed by independent fan coils and a global TABS coupling zone. Radiance and occupancy vary by zone. | Indoor air temperature | Component | Gray-Box | Same LLMN grey-box models used in control design | Same as process model | No | - | Yes | Real data | N/A | N/A | - | N/A | Supply temperature via Fan Coils per zone, TABS | Medium | Energy supply cost (based on heat flow); Comfort (temperature deviation from setpoint) | FMPC without cooperation (FMPCwo,c); Global linear MPC (MPClin); Historical rule-based PID controller | No | Simulation only | No | The process model and testbed are the same | THERMAL COMFORT; SYSTEMS | [Killian, M.; Kozek, M.] Vienna Univ Technol, Inst Mech & Mechatron, Getreidemarkt 9, A-1060 Vienna, Austria; [Mayer, B.] FH Joanneum, Werk VI Str 46, A-8605 Kapfenberg, Austria | Technische Universitat Wien | Killian, M (corresponding author), Vienna Univ Technol, Inst Mech & Mechatron, Getreidemarkt 9, A-1060 Vienna, Austria. | michaela.killian@tuwien.ac.at; barbara.mayer@fh-joanneum.at; martin.kozek@tuwien.ac.at | 43 | 43 | 112 |  |  |  | 130 | 140
127 | 127 | MPC control for improving energy efficiency of a building air handler for multi-zone VAVs | Liang, W; Quinte, R; Jia, XB; Sun, JQ | Liang, Wei; Quinte, Rebecca; Jia, Xiaobao; Sun, Jian-Qiao | OCT | 2015 | http://dx.doi.org/10.1016/j.buildenv.2015.04.033 | Building energy efficiency; Model predictive control; HVAC system; ARMAX model; Optimization | CO | Building and Environment | Standard AHU controls (e.g., local PID/economizer logic) don’t coordinate energy use with multi-zone VAV demands or handle cross-level constraints well; prior work often focuses on components or simulations rather than a system-level AHU model tied to real building data | 1. Build a system-level dynamic model of an AHU serving multi-zone VAVs using ARMAX for return-air temperature and flow; 2. Formulate an MPC that minimizes AHU energy (coil + fan) while tracking temperature/ventilation references and respecting constraints; 3. Validate with extensive measurements from UC Merced’s SE1 building and compare against the building’s baseline control. | Subsystem | VAV system | Subsystem | Black-Box | ARMAX for TRA and ṁ_RA | Sensible cooling only (dry Merced climate; dew point < 55°F) → no latent term; fan power via affinity law | Yes | Energy model for coil load and fan power | Yes | Real data | N/A | N/A | Virtual testbed | The virtual testbed is identical to the process model used in the MPC — a hybrid of two ARMAX models (TRA, ṁ_RA) identified from UC Merced SE1 AHU9 data, combined with static coil load and fan power equations. | VAV system | Subsystem | Black-Box | ARMAX for TRA and ṁ_RA | Sensible cooling only (dry Merced climate; dew point < 55°F) → no latent term; fan power via affinity law | Yes | Energy model for coil load and fan power | Yes | Real data | N/A | N/A | - | 15min | Recirculation damper ratio, supply-air temperature, outside-air flow | Medium | Setpoint-tracking errors, Energy saving | Original local PID/existing BAS control | No | Simulation only | No | The process model and testbed are the same | MODEL-PREDICTIVE CONTROL; OPTIMIZATION; STRATEGIES; SYSTEMS; PART; TEMPERATURE | [Liang, Wei; Quinte, Rebecca; Sun, Jian-Qiao] Univ Calif, Sch Engn, Merced, CA 95343 USA; [Jia, Xiaobao] Shenzhen Ploytech, Sch Mech & Elect Engn, Shenzhen 518055, Peoples R China | University of California System; University of California Merced | Sun, JQ (corresponding author), Univ Calif, Sch Engn, Merced, CA 95343 USA. | jqsun@ucmerced.edu | 68 | 76 | 92 |  |  |  | 256 | 268
128 | 128 | Fault-tolerant optimal control of a building HVAC system | Bengea, SC; Li, PF; Sarkar, S; Vichik, S; Adetola, V; Kang, K; Lovett, T; Leonardi, F; Kelman, AD | Bengea, Sorin C.; Li, Pengfei; Sarkar, Soumik; Vichik, Sergey; Adetola, Veronica; Kang, Keunmo; Lovett, Teems; Leonardi, Francesco; Kelman, Anthony D. | 2026-08-18 | 2015 | http://dx.doi.org/10.1080/23744731.2015.1057085 |  | CO | Science and Technology for the Built Environment | Building controls often handle optimal control (MPC) and fault detection & diagnosis (FDD) separately, driving up commissioning cost and missing coordinated responses to faults. There’s a need for an integrated, supervisory-level, fault-tolerant control (FTC) that adapts setpoints when actuators are faulty while preserving comfort and efficiency. See intro and motivation; also Figure 5 workflow. | 1. Develop and integrate data-driven FDD with supervisory MPC into a single FTC framework. 2. Deploy online on a large commercial HVAC system and report energy, demand, comfort, and FDD accuracy. 3. Reduce deployment cost by sharing sensors/platforms and using automated MPC formulation (BLOM → IPOPT). | Subsystem | Indoor air temperature | Component | Black-Box | Nonlinear ARX with exogenous inputs | Lumped air volume with ideal mixing | Yes | AHU/VAV subsystem | Yes | Real data | IPOPT, Berkeley Library for Optimization Modeling | MATLAB | Real building | Two identical large buildings at Navy Recruit Training Center, Great Lakes, IL, with 3 AHUs serving 57 VAVs. | - | - | - | - | - | - | - | - | - | - | - | Existing BMS (BACnet overrides for fault seeding), VFDs, added BTU meters, airflow stations, temperature sensors | 15min | VAV airflow setpoints, VAV reheat valve positions, AHU discharge-air temperature setpoint, OA & mixed-air damper positions | Medium, Low | Total energy & peak demand (electrical + thermal converted via COP), comfort violations (integral of temperature shortfall), FDD accuracy. | Baseline BMS schedules (matched by outdoor-air temperature patterns); MPC vs FTC under seeded OA-damper faults. | Yes | Full-scale real-world deployment | Yes | Model representation limit | MODEL-PREDICTIVE CONTROL; ENERGY; SIMULATION; IMPLEMENTATION; DIAGNOSTICS; COMPUTATION; PROGNOSTICS | [Bengea, Sorin C.; Adetola, Veronica; Kang, Keunmo] United Technol Corp, Control & Diagnost Syst, Pratt & Whitney, E Hartford, CT 06118 USA; [Li, Pengfei] United Technol Res Ctr, Thermofluid Dynam Grp, E Hartford, CT 06108 USA; [Sarkar, Soumik] Iowa State Univ, Dept Mech Engn, Ames, IA USA; [Vichik, Sergey; Kelman, Anthony D.] Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94720 USA; [Lovett, Teems; Leonardi, Francesco] United Technol Res Ctr, Embedded Syst Grp, E Hartford, CT 06108 USA | RTX Corporation; Pratt & Whitney; RTX Corporation; Iowa State University; University of California System; University of California Berkeley; RTX Corporation | Bengea, SC (corresponding author), United Technol Corp, Control & Diagnost Syst, Pratt & Whitney, 400 Main St, E Hartford, CT 06118 USA. | sbengea@ieee.org | 30 | 34 | 21 | 6 |  | SI | 734 | 751
129 | 129 | A new model predictive control scheme for energy and cost savings in commercial buildings: An airport terminal building case study | Huang, H; Chen, L; Hu, E | Huang, Hao; Chen, Lei; Hu, Eric | JUL | 2015 | http://dx.doi.org/10.1016/j.buildenv.2015.01.037 | Model predictive control; Neural network model; Energy efficiency; HVAC | CO | Building and Environment | MPC at building scale struggles with nonlinear, time-varying dynamics, uncertain disturbances (weather/occupancy), bilinear HVAC processes, and MIMO couplings; ANN-based MPCs are computationally heavy and hard to tune. | Propose a hybrid MPC (HMPC) that uses a linearized RC model for optimization + an inverse ANN for feedback linearization of HVAC nonlinearities; integrate supervisory strategies (economizer, optimal start/stop, load shifting); validate via simulations and a field experiment in an airport terminal. | Subsystem | Building thermal | Component | Gray-Box, Black-Box | RC (3R2C) network → linear state-space with Kalman innovation; parameters via nonlinear least-squares (grey-box ID); Inverse NARX-type MLP maps desired cooling capacity & recent states → real inputs of chilled-water valve and outdoor air damper position. | Uniform zone temperature; constant air density/flow; windows negligible capacitance; convective exchange between open zones dominates; coil air perfectly mixed; latent heat neglected; OA/RA mix ∝ damper position. | Yes | Economizer, Fan | Yes | Real data | YALMIP | MATLAB | Real building, Virtual testbed | Virtual testbed (forward ANN plant-in-the-loop), Real building (Adelaide Airport T1 check-in hall; four adjacent perimeter zones each with CAV AHU). | Indoor air temperature | Component | Black-Box | NARX/MLP (recurrent via tapped delays) trained on BMS data | Same measurement set & sampling (10 min); data normalized; delays set ≤ sampling interval. | No | - | Yes | Real data | N/A | MATLAB | Johnson Controls BMS | 10min | Chilled-water valve position, Outdoor air damper | Low | Energy use (AHU coil/fan), utility cost under TOU, peak-hour share of daily energy, comfort constraint satisfaction. | Baseline control (fixed setpoints & default economizer behavior) | Yes | Full-scale real-world deployment | Yes | Model representation limit | OPTIMAL TEMPERATURE CONTROL; NEURAL-NETWORK MODELS; THERMAL COMFORT; CONTROL-SYSTEMS; PART II; UNCERTAINTY; STORAGE | [Huang, Hao; Chen, Lei; Hu, Eric] Univ Adelaide, Sch Mech Engn, Adelaide, SA 5005, Australia | University of Adelaide | Huang, H (corresponding author), Univ Adelaide, Sch Mech Engn, Adelaide, SA 5005, Australia. | h.huang@adelaide.edu.au; lei.chen@adelaide.edu.au | 133 | 162 | 89 |  | 1 |  | 203 | 216
130 | 130 | A neural network-based multi-zone modelling approach for predictive control system design in commercial buildings | Huang, H; Chen, L; Hu, E | Huang, Hao; Chen, Lei; Hu, Eric | 2026-06-15 | 2015 | http://dx.doi.org/10.1016/j.enbuild.2015.03.045 | Multi-zone modelling; Artificial neural networks (ANNs); HVAC; Predictive control | CO | Energy and Buildings | Prior building models often target small/single-zone cases and miss inter-zone thermal coupling and nonlinear dynamics/uncertainties typical of real commercial buildings; simplified RC/linear ID models struggle here. | 1. Develop a multi-zone ANN (NARX) model that captures convective heat transfer between adjacent zones and key HVAC/weather inputs; 2. Compare single-zone vs multi-zone modelling accuracy; 3. Use the model as a virtual testbed to design a predictive optimal start–stop strategy and estimate energy savings. | Subsystem | Indoor air temperature | Component | Black-Box | MIMO NARX neural network (MLP) with forward input/lag selection | Fully mixed air in zones; constant air density/flow | No | - | Yes | Real data | N/A | MATLAB | Virtual testbed | Trained ANN model (multi-zone NARX–MLP) as the virtual building plus simplified coil and fan energy models | Indoor air temperature | Component | Black-Box | MIMO NARX–MLP | Same as process model | No | - | Yes | Real data | N/A | MATLAB | - | 10min | AHU start/stop timing | High | Temperature tracking within comfort band; estimated cooling energy | Fixed AHU schedule (04:00–22:00) | No | Simulation only | No | The process model and testbed are the same | PART I; ENERGY; TEMPERATURE; SAVINGS | [Huang, Hao; Chen, Lei; Hu, Eric] Univ Adelaide, Sch Mech Engn, Adelaide, SA 5005, Australia | University of Adelaide | Huang, H (corresponding author), Univ Adelaide, Sch Mech Engn, Adelaide, SA 5005, Australia. | h.huang@adelaide.edu.au; lei.chen@adelaide.edu.au | 117 | 128 | 97 |  |  |  | 86 | 97
131 | 131 | Online optimal control of variable refrigerant flow and variable air volume combined air conditioning system for energy saving | Zhu, YH; Jin, XQ; Du, ZM; Fang, X | Zhu, Yonghua; Jin, Xinqiao; Du, Zhimin; Fang, Xing | 2026-04-05 | 2015 | http://dx.doi.org/10.1016/j.applthermaleng.2015.01.030 | Combined air conditioning system; Variable refrigerant flow; Variable air volume; Optimal control; Adaptive model | CO | Applied Thermal Engineering | Few studies have integrated VRF systems with appropriate ventilation and jointly controlled both. Existing solutions either lack OA ventilation or operate ventilation and VRF parts separately, leading to inefficiencies. Limited work exists on model-based online optimal control for such combined systems. | 1. Propose a VRF + VAV combined air conditioning system with continuous OA flow control. 2. Develop simplified adaptive models for major components for online performance prediction. 3. Design and test a model-based online optimal control strategy using GA to minimize energy consumption while maintaining thermal comfort. | Subsystem | Indoor air temperature, IAQ | Component | Gray-Box | Simplified adaptive models | Solar radiation and window/envelope heat transfer not actively interacted. | Yes | Instantaneous cooling capacity, COP and energy consumption of VRF, OAP, and fan | Yes | Simulated data | N/A | N/A | Virtual testbed | TRNSYS white-box simulation of a 6-story multi-zone office building (Shanghai, China) with VRF + VAV OA processing system. | HVAC system | Whole System | White-Box | Integrated TRNSYS models for VRF, OAP, fan, building envelope, | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | 50s | OA supply temperature set-point | Medium | Energy consumption (VRF, OAP, fan), indoor temperature deviation, overall weighted cost (comfort + energy). | Conventional fixed OA supply temperature setpoint at 20 °C. | No | Simulation only | Yes | Model representation limit | GENETIC ALGORITHM; OUTDOOR AIR; PART I; COOLING CONDITIONS; SIMULATION-MODEL; PROCESSING UNIT; VRV SYSTEM; HEAT-PUMP; PERFORMANCE; VAV | [Zhu, Yonghua; Jin, Xinqiao; Du, Zhimin; Fang, Xing] Shanghai Jiao Tong Univ, Sch Mech Engn, Shanghai 200240, Peoples R China | Shanghai Jiao Tong University | Jin, XQ (corresponding author), Shanghai Jiao Tong Univ, Inst Refrigerat & Cryogen, 800 Rd Dong Chuan, Shanghai 200240, Peoples R China. | xqjin@sjtu.edu.cn | 25 | 29 | 80 |  |  |  | 87 | 96
132 | 132 | Model Predictive Control of Central Chiller Plant With Thermal Energy Storage Via Dynamic Programming and Mixed-Integer Linear Programming | Deng, K; Sun, Y; Li, SS; Lu, Y; Brouwer, J; Mehta, PG; Zhou, MC; Chakraborty, A | Deng, Kun; Sun, Yu; Li, Sisi; Lu, Yan; Brouwer, Jack; Mehta, Prashant G.; Zhou, MengChu; Chakraborty, Amit | APR | 2015 | http://dx.doi.org/10.1109/TASE.2014.2352280 | Central chiller plant; dynamic programming; heuristic algorithm; mixed integer linear programming; model predictive control; supervisory control; thermal energy storage | CO | IEEE Transactions on Automation Science and Engineering | Existing MPC frameworks for central chiller plants with TES often assume continuously adjustable chiller flow rates and fixed TES profiles, which do not reflect the practical ON/OFF scheduling of chillers and the variability of TES operation under real campus loads. Solving the resulting large-scale MINLPs in real time is computationally challenging. | 1. Formulate an MPC problem for a campus central chiller plant with TES to minimize electricity costs while meeting cooling demands. 2. Propose a heuristic solution combining Dynamic Programming (DP) for TES scheduling and MILP for chiller operation to achieve near-optimal solutions efficiently. | Subsystem | TES | Component | Gray-Box | State-space TES thermal | TES tank always full, inflow = outflow, no delay. | Yes | Chiller electricity consumption and COP; campus load balance. | Yes | Real data | N/A | MATLAB | Virtual testbed | UCI central chiller plant: multiple ON/OFF chillers, TES tank, campus load model | TES | Component | Gray-Box | State-space TES thermal | TES tank always full, inflow = outflow, no delay. | Yes | Chiller electricity consumption and COP; campus load balance. | Yes | Real data | N/A | MATLAB | - | 1h | ON/OFF status of each chiller; TES charging/discharging mode | Medium | Total electricity cost (TOU pricing), Total electricity consumption, COP | Greedy-search heuristic strategy using TES profile + chiller efficiency ranking. | No | Simulation only | No | The process model and testbed are the same | DESIGN OPTIMIZATION; HVAC SYSTEMS; CRUDE-OIL; ALGORITHM; OPERATION | [Deng, Kun; Mehta, Prashant G.] Univ Illinois, Dept Mech Sci & Engn, Urbana, IL 61801 USA; [Sun, Yu; Chakraborty, Amit] Siemens Corp, Corp Technol, Princeton, NJ 08540 USA; [Li, Sisi; Zhou, MengChu] New Jersey Inst Technol, Dept Elect & Comp Engn, Newark, NJ 07102 USA; [Zhou, MengChu] King Abdulaziz Univ, Dept Elect & Comp Engn, Jeddah 21413, Saudi Arabia; [Lu, Yan] NIST, Gaithersburg, MD 20899 USA; [Brouwer, Jack] Univ Calif Irvine, Dept Mech & Aerosp Engn, Irvine, CA 92697 USA | University of Illinois System; University of Illinois Urbana-Champaign; Siemens AG; Siemens USA; New Jersey Institute of Technology; King Abdulaziz University; National Institute of Standards & Technology (NIST) - USA; University of California System; University of California Irvine | Deng, K (corresponding author), Univ Illinois, Dept Mech Sci & Engn, Urbana, IL 61801 USA. | kundeng2@illinois.edu; yu.sun@siemens.com; sl98@njit.edu; yan.lu@nist.gov; jbrouwer@uci.edu; mehtapg@illi-nois.edu; zhou@njit.edu; amit.chakraborty@siemens.com | 94 | 105 | 12 | 2 |  |  | 565 | 579
133 | 133 | Exergy-based optimal control of a vapor compression system | Jain, N; Alleyne, A | Jain, Neera; Alleyne, Andrew | 2026-03-01 | 2015 | http://dx.doi.org/10.1016/j.enconman.2014.12.014 | Exergy destruction minimization; Control systems; Optimal control; Dynamic modeling; Vapor compression systems | CO | Energy Conversion and Management | 1. Exergy destruction minimization (EDM) has been extensively applied at the design stage for thermal systems, but not for closed-loop operation of vapor compression systems (VCSs). 2. COP-based optimization fails to capture true thermodynamic efficiency, particularly under transient conditions with high-frequency disturbances. | 1. Derive a transient exergy destruction rate model for a canonical VCS. 2. Design and implement the first exergy-based (second law) MPC for VCS control. 3. Compare second-law MPC to first-law (energy-based) MPC under transient conditions. | Subsystem | HX | Component | White-Box | Linearization of validated nonlinear Lumped Parameter Moving Boundary (LPMB) model around a nominal operating point; discretized in state-space form | Derived from LPMB model with quasi-steady compressor and EEV. Linearization about an equilibrium point. Air-side effects represented via refrigerant-side heat transfer coefficients. | Yes | Compressor, Expansion valve | No | None | Optimization Toolbox | MATLAB | Virtual testbed | Nonlinear simulation of a 1 kW capacity VCS with R134a refrigerant, semi-hermetic reciprocating compressor, EEV, condenser, evaporator, and variable-speed fans; validated against experimental system at the University of Illinois Urbana–Champaign. | HX | Component | White-Box | Lumped Parameter Moving Boundary (LPMB) for heat exchangers; quasi-steady compressor and EEV. | No heat transfer between different fluid regions within a heat exchanger. Reference temperature = ambient. Fan power excluded from exergy calculation. Air-side effects simplified through refrigerant-side heat transfer coefficients. | Yes | Compressor, Expansion valve | Yes | Lab | N/A | MATLAB | - | 1s | EEV aperture, Compressor speed, Evaporator air mass flow rate, Condenser air mass flow rate | Low | Exergetic efficiency, Exergy destruction rate, COP, Total energy consumption, Cooling capacity tracking error | First-law (energy-based) MPC | No | Simulation only | Yes | Demonstrates benefits of exergy-based MPC over energy-based MPC in transient operation. | MODEL-PREDICTIVE CONTROL | [Jain, Neera] Purdue Univ, W Lafayette, IN 47907 USA; [Alleyne, Andrew] Univ Illinois, Urbana, IL USA | Purdue University System; Purdue University; University of Illinois System; University of Illinois Urbana-Champaign | Jain, N (corresponding author), Purdue Univ, W Lafayette, IN 47907 USA. | neerajain@purdue.edu; alleyne@illinois.edu | 44 | 47 | 92 |  |  |  | 353 | 365
134 | 134 | Modeling and optimal control of an energy-efficient hybrid solar air conditioning system | Ha, QP; Vakiloroaya, V | Ha, Q. P.; Vakiloroaya, V. | JAN | 2015 | http://dx.doi.org/10.1016/j.autcon.2014.06.004 | Solar-assisted air-conditioner; Sub-cooling; Refrigerant mass flow rate; Air flow rate; Optimal control | CO | Automation in Construction | Previous solar-assisted air conditioning systems did not adequately address performance optimization under partial load conditions, especially regarding refrigerant sub-cooling control and integration with real-time control strategies. Limited studies examined using solar vacuum collectors after the compressor to influence system COP and energy performance. | 1. Develop a new configuration of a hybrid solar-assisted DX air conditioner with controllable refrigerant and condenser airflow rates. 2. Build a validated dynamic model of the reconfigured system. 3. Design and implement a multi-input multi-output optimal control scheme (LQR) to enhance energy efficiency and system performance. | Subsystem | Hybrid solar air conditioning system | Subsystem | White-Box | Lumped parameter model using mass and energy balance laws; linearized state-space form for control design. | Isentropic compressor operation. Lumped thermal capacitance per component. Constant heat transfer coefficients. | No | - | Yes | Real data | N/A | N/A | Virtual testbed | TRNSYS 16 simulation model of the hybrid solar-assisted DX air conditioner, validated using experimental data from the physical unit. | Hybrid solar air conditioning system | Subsystem | White-Box | Nonlinear lumped parameter model from mass and energy balances | Isentropic compressor, lumped capacitance, constant heat transfer coefficients. | No | - | Yes | Lab | N/A | TRNSYS | - | 20min | Refrigerant mass flow rate (via solenoid valve) and condenser fan speed (via VSD). | Low | Energy savings (%), COP improvement (%), refrigerant temperature reduction, supply air temperature. | Same system without control (open-loop baseline) simulated in TRNSYS. | No | Simulation only | Yes | Model representation limit | REFRIGERATION SYSTEM; PERFORMANCE; SIMULATION; STORAGE | [Ha, Q. P.; Vakiloroaya, V.] Univ Technol Sydney, Fac Engn & Informat Technol, Sydney, NSW 2007, Australia | University of Technology Sydney | Ha, QP (corresponding author), Univ Technol Sydney, Fac Engn & Informat Technol, POB 123 Broadway, Sydney, NSW 2007, Australia. | quang.ha@uts.edu.au | 17 | 17 | 49 |  | B | SI | 262 | 270
135 | 135 | Robust model-based fault diagnosis for air handling units | Mulumba, T; Afshari, A; Yan, R; Shen, W; Norford, LK | Mulumba, Timothy; Afshari, Afshin; Yan, Re; Shen, Wen; Norford, Leslie K. | JAN | 2015 | http://dx.doi.org/10.1016/j.enbuild.2014.10.069 | Fault detection and diagnosis; Air handling units; ARX model; Machine learning techniques; Parameter estimation; Recursive least squares | FDD | Energy and Buildings | Existing BMS often fail to detect non-catastrophic HVAC faults before scheduled maintenance and do not account for weather/schedule variability. Many model-based FDD approaches require numerous sensors or are not robust to model parameter uncertainty. | Develop a robust, low-sensor-count, parameter-based model using ARX modeling and SVM classification to detect and diagnose common AHU faults with high accuracy and low false alarm rates, while maintaining robustness to parameter uncertainty. | Component | AHU | Component | Black-Box | ARX (autoregressive with exogenous inputs) model identified using recursive least squares with forgetting factor. | System reaches stationary state before each fault occurs. Transition from normal to faulty operation does not alter basic structure of the system—only parameters change. | No | - | Yes | Real data | N/A | N/A | Historical data | ASHRAE project 1312-RP dataset | - | - | - | - | - | - | - | - | - | - | - | - | 1min | - | - | Precision, Recall, F-measure | Compared against raw-data-based LibSVM, Naive Bayes, Bayesian Network, RBF network, multilayer perceptron, random forest, random tree. | No | Historical data | Yes | Model representation limit | QUANTITATIVE MODEL; SYSTEMS; ARX; IDENTIFICATION; METHODOLOGY; VALIDATION; NETWORK; AHU | [Mulumba, Timothy; Afshari, Afshin; Yan, Re; Shen, Wen] Masdar Inst Sci & Technol, Dept Engn Syst & Management, Abu Dhabi, U Arab Emirates; [Norford, Leslie K.] MIT, Dept Architecture, Cambridge, MA 02139 USA | Khalifa University of Science & Technology; Masdar Institute of Science & Technology; Massachusetts Institute of Technology (MIT) | Afshari, A (corresponding author), Masdar Inst Sci & Technol, Dept Engn Syst & Management, POB 54224, Abu Dhabi, U Arab Emirates. | aafshari@masdar.ac.ae | 104 | 118 | 86 |  |  |  | 698 | 707
136 | 136 | A fast chiller power demand response control strategy for buildings connected to smart grid | Xue, X; Wang, SW; Yan, CC; Cui, BR | Xue, Xue; Wang, Shengwei; Yan, Chengchu; Cui, Borui | 2026-01-01 | 2015 | http://dx.doi.org/10.1016/j.apenergy.2014.09.084 | Building demand response; Fast demand response; Chiller power demand limiting; HVAC system control; Building thermal storage; Smart grid | EF | Applied Energy | 1. Existing demand response (DR) strategies in buildings often rely on indoor air temperature setpoint reset, which causes significant delays and cannot meet the real-time needs of the electrical grid. 2. Shutting down chillers directly can cause disordered chilled water flow and uneven indoor comfort degradation. 3. Limited studies on fast demand response in commercial buildings with coordinated control of both water side and air side to maintain comfort. | 1. Develop a fast chiller power demand response control strategy for commercial buildings to act as spinning reserves for the smart grid, responding within minutes. 2. Use dynamic models to estimate building cooling demand reduction, chiller power demand reduction, and allowable duration of demand limiting. 3. Address chilled water distribution imbalance and uneven comfort during rapid chiller shutdown events. | Whole System | Building thermal | Component | Gray-Box | Grey-box RC-network model (3R2C for envelope, 2R2C for internal thermal mass). Lumped-capacitance thermal storage model for load shifting potential. | Building as lumped zones with homogeneous thermal mass. | Yes | Chiller | Yes | Simulated data | N/A | N/A | Virtual testbed | TRNSYS-based dynamic simulation of a large commercial office building in Hong Kong climate; 90 floors (1600 m² each), central chiller plant with 6 water-cooled centrifugal chillers (7230 kW each), secondary/primary pumps, 90 AHUs serving different zones. | HVAC system | Whole System | White-Box | TRNSYS component-level modeling of HVAC and building envelope. | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | N/A | Set-points of water loop pressure and the valve openings of AHUs | Medium | Power demand reduction (kW and % of baseline). Duration of DR event before comfort limit breach. Indoor thermal comfort indices (PMV, PPD). Daily HVAC energy savings | Conventional control without DR measures. Variants with only water side control, only air side control | No | Simulation only | Yes | Model representation limit | THERMAL STORAGE; WATER-SYSTEMS; ENERGY; MODEL | [Xue, Xue; Wang, Shengwei; Yan, Chengchu; Cui, Borui] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China | Hong Kong Polytechnic University | Wang, SW (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | beswwang@polyu.edu.hk | 114 | 125 | 137 |  |  |  | 77 | 87
137 | 137 | Dynamic frequency regulation resources of commercial buildings through combined building system resources using a supervisory control methodology | Zhao, P; Henze, GP; Brandemuehl, MJ; Cushing, VJ; Plamp, S | Zhao, Peng; Henze, Gregor P.; Brandemuehl, Michael J.; Cushing, Vincent J.; Plamp, Sandro | JAN | 2015 | http://dx.doi.org/10.1016/j.enbuild.2014.09.078 | Building to grid integration; Frequency regulation; Demand side management; HVAC system modeling and control; Supervisory control | EF | Energy and Buildings | 1. Limited research on using large commercial building HVAC systems as fast and accurate frequency regulation (FR) resources, compared to costly storage devices (e.g., batteries, flywheels). 2. Lack of supervisory control strategies that can coordinate interdependent HVAC subsystems to provide FR while respecting capacity, comfort, and market constraints. | 1. Develop and evaluate a model-based supervisory control for commercial HVAC systems to participate in PJM’s RegD frequency regulation market. 2. Model the building/HVAC system to determine baseline power, available regulation capacity, and optimal FR participation levels (PLs) in real time. 3. Compare single- and multiple-injection FR control strategies via simulation to maximize FR revenue while maintaining comfort. | Whole System | Building thermal, IAQ, HVAC pipe network | Component | White-Box | Thermal zones: 3R2C RC network per opaque element. Waterside: chilled water loop with two-chiller sequencing, pipe (represented by storage tank) as first-order mixed volumes. | Building tightly insulated; infiltration rate zero during HVAC hours. | Yes | VAV airside, Chiller | No | None | N/A | MATLAB | Virtual testbed | Simulated 1M ft² high-rise commercial office building HVAC system in MATLAB/Simulink, matching the process model structure. Includes five-zone thermal model, VAV airside, chilled water plant with two chillers, and empirical equipment power models. Driven by real weather (Chicago, July 10, 2013) and PJM RegD signal/pricing. | Building thermal, IAQ, HVAC pipe network | Subsystem | White-Box | Same as process model | Same as process model | Yes | VAV airside, Chiller | No | None | Simulink | MATLAB | - | 1h | Static pressure setpoint, Zone temperature setpoint, Discharge air temperature setpoint, Outside air fraction setpoint | Medium, High | PJM performance score (correlation, delay, precision), FR capacity (kW), Revenue from capacity and performance payments, Thermal comfort | Single-injection vs. multiple-injection methods; participation levels (PLs) varied. (comparison is between method variants) | No | Simulation only | No | The process model and testbed are the same |  | [Zhao, Peng; Henze, Gregor P.; Brandemuehl, Michael J.] Univ Colorado, Boulder, CO 80309 USA; [Cushing, Vincent J.; Plamp, Sandro] QCoefficient Inc, Chicago, IL 60605 USA | University of Colorado System; University of Colorado Boulder | Zhao, P (corresponding author), Univ Colorado, Boulder, CO 80309 USA. | peng.zhao@colorado.edu; gregor.henze@colorado.edu; michael.brandemuehl@colorado.edu; vince@qcoefficient.com; sandro@qcoefficient.com | 47 | 55 | 86 |  |  |  | 137 | 150
138 | 138 | Hybrid model predictive control of stratified thermal storages in buildings | Berkenkamp, F; Gwerder, M | Berkenkamp, Felix; Gwerder, Markus | DEC | 2014 | http://dx.doi.org/10.1016/j.enbuild.2014.07.052 | Hybrid model predictive control; Building control; Stratified thermal storage; Free/passive cooling | CO | Energy and Buildings | Conventional rule-based control for stratified thermal storages lacks advanced storage management capabilities, often ignoring stratification effects and requiring restrictive assumptions. Existing MPC approaches for buildings focus on whole-building optimization or passive thermal mass, with limited work on detailed stratified storage models integrated with modular generation systems. | Propose a modular hybrid MPC algorithm for stratified water storage management in buildings that: 1. Operates independently of building thermal control. 2. Uses short-term load forecasting and weather data. 3. Manages generation/consumption via discrete operating modes for computational efficiency. 4. Requires minimal instrumentation and plant information while maintaining close-to-optimal performance. | Subsystem | TES | Component | White-Box | Stratified storage tank thermal model with nonlinear heat transfer, mass flow, and conduction equations; discretized into n layers; includes conduction, losses, and convective flows between layers. | Fixed number of layers with lumped mass/temperature per layer. Ambient heat loss modeled via constant resistances. Known key tank parameters; limited sensors available (state estimation required). Inversion modeled as reduced thermal resistance between layers. | No | - | No | None | N/A | N/A | Virtual testbed | Simulated 25 m³ stratified cold water storage tank with 10 layers; connected to one chiller (2 kW) and one cooling tower. Cold consumers modeled as chilled ceilings in ∼200 m² office space, with known future demand (from measurement). | TES | Component | White-Box | Same as process model — lumped-parameter stratified tank model. | Same as process model | No | - | No | None | N/A | N/A | - | 1h | Cooling tower mass flow, Chiller on/off | Medium | Energy cost, equipment wear, temperature constraint satisfaction. | None | No | Simulation only | No | The process model and testbed are the same | ENERGY STORAGE; OPTIMIZATION; SYSTEMS; WEATHER | [Berkenkamp, Felix; Gwerder, Markus] Siemens Switzerland Ltd, Div Bldg Technol, CH-6301 Zug, Switzerland | Siemens AG | Gwerder, M (corresponding author), Siemens Switzerland Ltd, Div Bldg Technol, Gubelstr 22, CH-6301 Zug, Switzerland. | befelix@ethz.ch; markus.gwerder@siemens.com | 25 | 25 | 84 |  |  |  | 233 | 240
139 | 139 | Integrating scheduling and control for economic MPC of buildings with energy storage | Touretzky, CR; Baldea, M | Touretzky, Cara R.; Baldea, Michael | AUG | 2014 | http://dx.doi.org/10.1016/j.jprocont.2014.04.015 | Hierarchical MPC; Scheduling; Economic MPC; Energy storage; Building systems | EF | Journal of Process Control | Existing MPC approaches for HVAC with thermal energy storage (TES) face computational challenges due to long prediction horizons (needed for weather/price forecasts) and discrete operating modes (binary decision variables). Centralized E-MPC with detailed nonlinear models becomes computationally prohibitive for real-time implementation. | Propose a hierarchical E-MPC framework for buildings with active TES that separates slow-timescale TES scheduling from fast-timescale indoor temperature control. Reduce computational load via continuous reformulation of the scheduling problem and demonstrate feasibility through a detailed simulation of the University of Texas Thermal Façade Lab (TFL). | Subsystem | TES, Building thermal, HX, Chiller | Subsystem | White-Box | First-principles physics models (energy balance PDEs for TES tank; ODEs for zone, thermal mass, coil, chiller). | TES tank well-mixed radially with a fixed thermocline separating hot/cold layers. Neglect heat conduction outside thermocline. Single-zone building modeled as well-mixed volume with lumped thermal mass. Fixed operating mode sequences (charge, discharge, idle) with continuous operation during each phase. | No | - | No | None | N/A | gPROMS | Virtual testbed | Simulated University of Texas Thermal Façade Lab (single-zone prototype building with detailed measurements, chilled water tank in HVAC loop). | TES, Building thermal, HX, Chiller | Subsystem | White-Box | Same first-principles PDE/ODE formulation as process model. | Same as process model | No | - | No | None | N/A | gPROMS | - | 24h | Zone temperature setpoint, TES mode (charge/discharge/idle), chiller cooling load, coil flow rates. | Medium, High | Energy cost reduction, peak load shifting, TES utilization, comfort limit violations. | Heuristic TES operation and different TES capacities/modes. | No | Simulation only | No | The process model and testbed are the same | MODEL-PREDICTIVE CONTROL; DYNAMIC OPTIMIZATION PROBLEMS; PERFORMANCE; SYSTEMS; DEMAND | [Touretzky, Cara R.; Baldea, Michael] Univ Texas Austin, McKetta Dept Chem Engn, Austin, TX 78712 USA | University of Texas System; University of Texas Austin | Baldea, M (corresponding author), Univ Texas Austin, McKetta Dept Chem Engn, 200 East Dean Keeton St,Stop C0400, Austin, TX 78712 USA. | mbaldea@che.utexas.edu | 117 | 126 | 24 | 8 |  | SI | 1292 | 1300
140 | 140 | Ancillary Service to the Grid Through Control of Fans in Commercial Building HVAC Systems | Hao, H; Lin, YS; Kowli, AS; Barooah, P; Meyn, S | Hao, He; Lin, Yashen; Kowli, Anupama S.; Barooah, Prabir; Meyn, Sean | JUL | 2014 | http://dx.doi.org/10.1109/TSG.2014.2322604 | Ancillary service; commercial buildings; demand response; frequency regulation; HVAC system | EF | IEEE Transactions on Smart Grid | Limited research exists on providing high-frequency ancillary services (seconds–minutes) from commercial building HVAC systems, despite their large thermal inertia, VFD-equipped fans, and widespread Building Automation Systems. Prior work mainly focuses on low-frequency load changes like peak shaving and open-loop demand response. | 1. Demonstrate that supply fans in commercial buildings can provide substantial frequency regulation with minimal indoor environment impact. 2. Propose a feedforward control architecture to manipulate fan speed for tracking grid regulation signals. 3. Develop simplified control-oriented models and validate the control on a high-fidelity nonlinear simulation of a real building. 4. Quantify regulation potential and inherent bandwidth limitations for such services. | Subsystem | Indoor air temperature, Fan | Component | Gray-Box | Fan: cubic speed-power relation with VFD dynamics (first-order); Simplified lumped thermal RC model for building dynamics (linearized for controller design) | Fan speed affects only high-frequency dynamics; chiller/cooling tower power consumption unaffected due to slow dynamics. All zones in Cooling Mode (no reheating). Building temperature controller senses desired fan speed directly, sidestepping duct pressure dynamics. | No | - | Yes | Real data, Simulated data | N/A | N/A | Virtual testbed | High-fidelity nonlinear multi-zone thermal model representing “F-building,” based on data from Pugh Hall (University of Florida). Modeled with 44 zones (4 stories × 11 zones per story) and a single AHU with VFD-driven fan. | Building thermal, Fan | Component | Gray-Box | RC-network thermal models for each zone; Same first-order fan model | All zones in cooling mode, Neglect reheating, Uniform fan air distribution ratio per zone | No | - | Yes | Real data | N/A | N/A | - | 4s | Fan speed | Low | Root mean squared tracking error (RMSE) between commanded and actual fan power deviation; Zone temperature deviation from setpoint; Potential regulation capacity (% of rated fan power) | Baseline building operation without regulation control | No | Simulation only | Yes | Model representation limit | DEMAND | [Hao, He; Lin, Yashen; Barooah, Prabir] Univ Florida, Dept Mech & Aerosp Engn, Gainesville, FL 32611 USA; [Kowli, Anupama S.] Indian Inst Technol, Dept Elect Engn, Bombay 400076, Maharashtra, India; [Meyn, Sean] Univ Florida, Dept Elect & Comp Engn, Gainesville, FL 32611 USA | State University System of Florida; University of Florida; Indian Institute of Technology System (IIT System); Indian Institute of Technology (IIT) - Bombay; State University System of Florida; University of Florida | Hao, H (corresponding author), Univ Calif Berkeley, Dept Elect Engn & Comp Sci, Berkeley, CA 94720 USA. | hehao@berkeley.edu | 194 | 220 | 5 | 4 |  |  | 2066 | 2074
141 | 141 | Handling model uncertainty in model predictive control for energy efficient buildings | Maasoumy, M; Razmara, M; Shahbakhti, M; Vincentelli, AS | Maasoumy, M.; Razmara, M.; Shahbakhti, M.; Vincentelli, A. Sangiovanni | JUL | 2014 | http://dx.doi.org/10.1016/j.enbuild.2014.03.057 | Modeling uncertainty; Building control; Model predictive control; Building HVAC system; Kalman filter | CO | Energy and Buildings | MPC performance in buildings is highly sensitive to model inaccuracies caused by time-varying parameters (e.g., occupancy, weather, internal gains). Accurate physical modeling is expensive and time-consuming, and controllers often lack robustness to these changes. No prior work has combined online adaptive modeling with robust MPC for buildings in a unified framework. | 1. Develop a Parameter Adaptive Building (PAB) model that estimates states and time-varying parameters online using an Unscented Kalman Filter (UKF). 2. Formulate a Robust MPC (RMPC) using a disturbance feedback parameterization (TLDS) to efficiently handle model uncertainty. 3. Quantify the effect of model uncertainty on MPC performance. 4. Provide guidelines for choosing between MPC, RMPC, and rule-based control based on model uncertainty level. | Subsystem | Building thermal | Component | Gray-Box | Lumped RC-network model with time-varying parameters; online parameter estimation via Unscented Kalman Filter (UKF). | Uniform temperature inside each room. Constant air ventilation rate. Wall material properties and thickness assumed uniform across building. | No | - | Yes | Real data | YALMIP | MATLAB | Virtual testbed | Single office room in the Lakeshore building, Michigan Technological University. Heated by a ground-source heat pump (GSHP). Two south-facing double-glass windows. | Building thermal | Component | Gray-Box | Lumped RC-network model with time-varying parameters; online parameter estimation via Unscented Kalman Filter (UKF). | Uniform temperature inside each room. Constant air ventilation rate. Wall material properties and thickness assumed uniform across building. | No | - | Yes | Real data | N/A | MATLAB | - | 1h | Air mass flow rate and supply air temperature | Medium | Energy index (Ie) [kWh] (heating, cooling, fan). Discomfort index (Id) [°C·h]. Overall Performance Index (IOP) combining Ie and Id. | Conventional rule-based on/off HVAC control. | No | Simulation only | No | The process model and testbed are the same | TEMPERATURE CONTROL; THERMAL COMFORT; OPTIMIZATION; SYSTEMS; STATE | [Maasoumy, M.] Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94703 USA; [Razmara, M.; Shahbakhti, M.] Michigan Technol Univ, Dept Mech Engn Engn Mech, Houghton, MI 49931 USA; [Vincentelli, A. Sangiovanni] Univ Calif Berkeley, Dept Elect Engn & Comp Sci, Berkeley, CA 94703 USA | University of California System; University of California Berkeley; Michigan Technological University; University of California System; University of California Berkeley | Maasoumy, M (corresponding author), Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94703 USA. | mehdi@me.berkeley.edu; mrazmara@mtu.edu; mandish@mtu.edu; alberto@eecs.berkeley.edu | 190 | 248 | 77 |  |  |  | 377 | 392
142 | 142 | Energy efficient control of HVAC systems with ice cold thermal energy storage | Beghi, A; Cecchinato, L; Rampazzo, M; Simmini, F | Beghi, Alessandro; Cecchinato, Luca; Rampazzo, Mirco; Simmini, Francesco | JUN | 2014 | http://dx.doi.org/10.1016/j.jprocont.2014.01.008 | HVAC; Thermal energy storage; Modeling; Control | CO | Journal of Process Control | Thermal energy storage (TES) control in HVAC systems often suffers from low energy efficiency and poor load satisfaction due to inadequate control design. Classical strategies struggle with nonlinear and strongly coupled dynamics. | 1. Develop a model-based control framework for HVAC with ice cold TES (CTES). 2. Create a hybrid model for ice CTES that includes both latent and sensible heat effects. 3. Compare standard control strategies with a nonlinear MPC using particle swarm optimization (PSO) in a realistic virtual testbed. | Subsystem | HVAC pipe network, TES | Subsystem | White-Box | Lumped-parameter conservation equations for each plant component combined into a discrete-time nonlinear state-space form | TES modeled as lumped temperature with both latent (~90%) and sensible heat storage. Constant thermophysical properties per phase. Well-mixed or stratified tank sections depending on volume fraction. | No | - | No | None | N/A | MATLAB | Virtual testbed | Simulated HVAC plant for a typical commercial building with two parallel air-cooled chillers, ice CTES, modulating valve, diverting valve, tank/piping, and conventional air-conditioning load. | HVAC pipe network, TES | Component | White-Box | Lumped-parameter conservation equations | Well-mixed or stratified tank sections depending on volume fraction. | Yes | Chiller, Valves | No | None | Simulink | MATLAB | - | 15min | Part load ratio (PLR) of chillers; TES bypass valve opening | Medium, Low | Normalized electricity bill, cooling demand satisfaction, energy use. | Constant-proportion control (P), Chiller-priority control (C), Storage-priority control (S) | No | Simulation only | No | The process model and testbed are the same | PERFORMANCE | [Beghi, Alessandro; Rampazzo, Mirco; Simmini, Francesco] Univ Padua, Dipartimento Ingn Informaz, I-35131 Padua, Italy; [Cecchinato, Luca] Everest Srl, I-133170 Pordenone, Italy | University of Padua | Rampazzo, M (corresponding author), Univ Padua, Dipartimento Ingn Informaz, Via Gradenigo 6-B, I-35131 Padua, Italy. | beghi@dei.unipd.it; lcecchinato@energyeverest.com; mirco.rampazzo@dei.unipd.it; simminif@dei.unipd.it | 48 | 56 | 24 | 6 |  | SI | 773 | 781
143 | 143 | A real-time model predictive control for building heating and cooling systems based on the occupancy behavior pattern detection and local weather forecasting | Dong, B; Lam, KP | Dong, Bing; Lam, Khee Poh | FEB | 2014 | http://dx.doi.org/10.1007/s12273-013-0142-7 | model predictive control; occupancy behavior patterns; weather forecasting; real-time implementation | CO | Building Simulation | Most existing MPC-based building control studies rely on historical or coarse weather data (often from distant stations) and fixed or assumed occupancy schedules. Few integrate short-term local weather forecasting (temperature, solar radiation, wind speed) with real-time occupant behavior detection for both heating and cooling. Additionally, the role of occupancy pattern prediction in optimizing control schedules in real-time is underexplored, especially for systems with very different response times (radiant floor heating vs. air-based cooling). | 1. Develop an integrated MPC for building heating and cooling that combines: Local weather forecasting (temp., solar radiation, wind speed), Occupancy behavior pattern detection (number & duration); 2. Build and validate a gray-box dynamic building and HVAC model for real-time NMPC use. 3. Implement and test the approach in a real Solar House testbed for heating and cooling seasons. 4. Quantify energy savings and comfort performance compared to conventional scheduled set-point control. | Subsystem | Building thermal | Component | Gray-Box | 3R2C gray-box thermal network for each wall and zone; Thermal capacitance–resistance model for concrete slab, plus heat transfer equations (conduction, convection, radiation). | Thermal properties time-invariant, Window thermal storage neglected (resistance only), Well-insulated floor (no ground heat loss) | Yes | Tankless water heater, Cooling fan coil unit + heat pump | Yes | Real data | Simulink | MATLAB | Real building | Solar House in Pittsburgh, PA (67.5 m², meeting room + office + ancillary spaces, radiant floor heating, fan coil cooling, SIP and polycarbonate walls, extensive sensor network measuring environmental, occupancy, and HVAC variables). | - | - | - | - | - | - | - | - | - | - | - | LabVIEW-based data acquisition system, Wireless environmental sensor network, Campbell Scientific CR1000 data logger system, Outdoor local weather station | Heating: 1 h, Cooling: 15 min | Model: Hot water temperature rise, Water flow rate, Supply air temperature, Airflow rate of fan coil unit; Implemented: Indoor heating temperature set-point, Indoor cooling temperature set-point | Medium, High | Energy consumption, comfort (hours set-point not met) | Scheduled temperature set-point control with night set-back. | Yes | Full-scale real-world deployment | Yes | Model representation limit | ENERGY; STORAGE | [Dong, Bing] Univ Texas San Antonio, Dept Mech Engn, San Antonio, TX 78294 USA; [Lam, Khee Poh] Carnegie Mellon Univ, Sch Architecture, Pittsburgh, PA 15213 USA | University of Texas System; University of Texas at San Antonio (UTSA); Carnegie Mellon University | Dong, B (corresponding author), Univ Texas San Antonio, Dept Mech Engn, San Antonio, TX 78294 USA. | bing.dong@utsa.edu | 212 | 242 | 7 | 1 |  |  | 89 | 106
144 | 144 | Decentralized model predictive control of a multi-evaporator air conditioning system | Elliott, MS; Rasmussen, BP | Elliott, Matthew S.; Rasmussen, Bryan P. | DEC | 2013 | http://dx.doi.org/10.1016/j.conengprac.2013.08.010 | Decentralized control; Predictive control; Efficiency; Architectures; Multiobjective optimizations | CO | Control Engineering Practice | Temperature control across multiple zones sharing a single vapor-compression system suffers from strong cross-coupling; decoupled SISO loops can fight each other and ignore constraints and efficiency. Implementing fully centralized control is also impractical in spatially distributed multi-evaporator systems. | Propose and experimentally validate a two-level, decentralized MPC architecture: a supervisory MPC that allocates cooling/pressure/superheat setpoints to balance zone tracking and energy efficiency, and local MPC/PID loops that track evaporator cooling while keeping superheat within bounds. Demonstrate tunability between comfort and energy, constraint handling (e.g., superheat band), and modularity. | Subsystem | Building thermal, HX | Subsystem | Gray-Box, Black-Box | Zones: first-order discrete-time RC-like lumped capacitance. Local plants: identified 2-in/2-out state-space models (inputs: EEV position, fan/pump speed; outputs: cooling, superheat). | Time-scale separation (VCC faster than zone), superheat maintained within a band (no exact tracking needed) | Yes | Inverse COP (ICOP) | Yes | Lab | MPC Toolbox | MATLAB | Lab | Three 1.5 kW evaporators cooling three 50 L water tanks as zones; single condenser with variable-speed compressor (max ≈3.75 kW). | - | - | - | - | - | - | - | - | - | - | - | N/A | Local MPC sample time: 8s; Supervisory MPC sample time: 300s | Cooling/pressure/superheat setpoints; EEV and fan/pump speed | Medium, Low | Zone temperature tracking, power/energy consumption and ICOP, superheat constraint satisfaction, disturbance rejection, demand shedding behavior. | None | Partial | Lab setup | Yes | Model representation limit |  | [Elliott, Matthew S.; Rasmussen, Bryan P.] Texas A&M Univ, Dept Mech Engn, College Stn, TX 77843 USA | Texas A&M University System; Texas A&M University College Station | Rasmussen, BP (corresponding author), TAMU 3123, College Stn, TX 77843 USA. | brasmussen@tamu.edu | 55 | 61 | 21 | 12 |  | SI | 1665 | 1677
145 | 145 | Model-based predictive control of an ice storage device in a building cooling system | Candanedo, JA; Dehkordi, VR; Stylianou, M | Candanedo, J. A.; Dehkordi, V. R.; Stylianou, M. | NOV | 2013 | http://dx.doi.org/10.1016/j.apenergy.2013.05.081 | Model predictive control; Thermal energy storage; Ice storage; Simplified modelling; System identification; Building simulation | CO | Applied Energy | Existing ice-storage building cooling plants often use simple rule-based strategies (storage-priority or chiller-priority) that don’t leverage forecasts or plant/building dynamics; better strategies are needed to optimally coordinate chiller and TES under time-varying electricity prices | 1. Derive a simplified linear building thermal model via system identification from an EnergyPlus model; 2. compute required cooling power from forecasts and setpoint trajectory; 3. formulate an MPC that optimally splits cooling between chiller and ice bank using simple chiller/TES models to minimize cost under TOU pricing, and also introduces variable-length horizons (24/30 h) aligned with charge/discharge cycles. | Subsystem | Indoor air temperature, TES | Subsystem | Black-Box | Building: Discrete transfer functions converted to state-space and inverted to compute required cooling load; TES: SOC dynamic update equation combined with operating mode. | Building dynamics approximated linear; constant capacity limits and stage logic. | Yes | Chiller | Yes | Simulated data | System Identification Toolbox, YALMIP | MATLAB | Virtual testbed | Simulated 5,300 m² one-story commercial building with chiller (R-22, ~180 kW) and ice bank (190 TR-h) modeled in MATLAB | Indoor air temperature, TES | Subsystem | Black-Box | Building: Discrete transfer functions converted to state-space and inverted to compute required cooling load; TES: SOC dynamic update equation combined with operating mode. | Building dynamics approximated linear; constant capacity limits and stage logic. | Yes | Chiller | Yes | Simulated data | N/A | MATLAB | - | 1h | Chiller cooling power, Ice-bank cooling power | Medium | Electricity cost of chiller under TOU pricing (objective), with comfort enforced via temperature-tracking constraints | Two rule-based baselines—Modified storage-priority (MSP) and Chiller-priority (CP) | No | Simulation only | No | The process model and testbed are the same | THERMAL STORAGE; HEATING-SYSTEM; REDUCTION; MANAGEMENT | [Candanedo, J. A.; Dehkordi, V. R.] Nat Resources Canada, CanmetENERGY Varennes, Varennes, PQ J3X 1S6, Canada; [Stylianou, M.] Nat Resources Canada, CanmetENERGY Ottawa, Ottawa, ON K1A 1M1, Canada | Natural Resources Canada; CanmetENERGY; Natural Resources Canada; CanmetENERGY | Candanedo, JA (corresponding author), Nat Resources Canada, CanmetENERGY Varennes, 1615 Lionel Boulet,CP 4800, Varennes, PQ J3X 1S6, Canada. | jose.candanedo@nrcan.gc.ca | 104 | 119 | 111 |  |  |  | 1032 | 1045
146 | 146 | Analysis of local optima in predictive control for energy efficient buildings | Kelman, A; Ma, YD; Borrelli, F | Kelman, Anthony; Ma, Yudong; Borrelli, Francesco | 2026-05-01 | 2013 | http://dx.doi.org/10.1080/19401493.2012.671959 | model predictive control; optimization; HVAC | CO | Journal of Building Performance Simulation | MPC for building HVAC uses simplified physics models that make the optimization non-convex; fast solvers only guarantee local optimality, which can yield worse performance than conventional control. Systematic understanding and mitigation of local optima is lacking. | 1. Formulate simplified physics-based models for two common HVAC configurations; 2. demonstrate and analyze local optima via simulation; 3. derive physics-based rules to exclude classes of locally-optimal solutions a priori (scenarios S1–S4 and elimination algorithm); 4. study how discretization (FE, trapezoidal, exact) affects existence/number/shape of local optima. | Subsystem | Indoor air temperature | Component | White-Box | First-order zone energy balance per zone (lumped capacitance) + mixing | First-order lumped zones; ignore humidity; actuator dynamics neglected; perfect forecasts of loads and weather. | Yes | Coil and fan power; mixed/return air temperatures | No | None | YALMIP, IPOPT | MATLAB | Virtual testbed | 3 zones with two HVAC configurations: A: Dual-duct, single fan (CAV with VFD). B: Single-duct VAV with reheat. | Indoor air temperature | Component | White-Box | First-order zone energy balance per zone (lumped capacitance) + mixing | First-order lumped zones; ignore humidity; actuator dynamics neglected; perfect forecasts of loads and weather. | Yes | Coil and fan power; mixed/return air temperatures | No | None | N/A | MATLAB | - | 30min | Config A: total supply flow, outside air flow , cooling setpoint , heating setpoint, zone mixing-box supply setpoints; Config B: zone flows, zone reheats | Medium | Total utility cost | None | No | Simulation only | No | The process model and testbed are the same |  | [Kelman, Anthony; Ma, Yudong; Borrelli, Francesco] Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94720 USA | University of California System; University of California Berkeley | Kelman, A (corresponding author), Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94720 USA. | kelman@berkeley.edu | 27 | 54 | 6 | 3 |  |  | 236 | 255
147 | 147 | Energy-efficient HVAC systems: Simulation-empirical modelling and gradient optimization | Vakiloroaya, V; Ha, QP; Samali, B | Vakiloroaya, V.; Ha, Q. P.; Samali, B. | MAY | 2013 | http://dx.doi.org/10.1016/j.autcon.2012.12.006 | Central cooling plant; Experimental study; Gradient projection method; Energy savings; Comfort | CO | Automation in Construction | Practical, plant-level optimal control strategies for chilled-water systems that explicitly co-optimize energy and comfort are still sparse; component interactions and transient behavior make physics-only models burdensome for operation. | 1. Build valid physical–empirical (gray-box) models of key central cooling-plant components; 2. formulate a gradient projection–based optimizer to minimize total power while meeting comfort; 3. implement the algorithm within TRNSYS and evaluate using field-measured data from an office building. | Whole System | FCU | Component | Gray-Box | Energy balances for water/air | Fan power regression | Yes | Air-cooled chiller, Water pumps | Yes | Real data | TRNOPT/GenOpt | TRNSYS | Virtual testbed | TRNSYS simulation of the plant | FCU | Component | White-Box | Energy balances for water/air | Fan power regression | Yes | Air-cooled chiller | Yes | Real data | MINITAB | TRNSYS | - | 15min | Supply chilled-water temperature, supply-air temperature, refrigerant mass flow rate | Medium | Total power consumption (compressor + condenser fan + fan-coil fan); thermal comfort via PMV. | Conventional/default operation | No | Simulation only | No | The process model and testbed are the same | WATER CHILLERS; PERFORMANCE; OPERATION | [Vakiloroaya, V.; Ha, Q. P.] Univ Technol Sydney, Sch Elect Mech & Mechatron Syst, Sydney, NSW 2007, Australia; [Samali, B.] Univ Technol Sydney, Sch Civil & Environm Engn, Sydney, NSW 2007, Australia | University of Technology Sydney; University of Technology Sydney | Ha, QP (corresponding author), POB 123, Sydney, NSW 2007, Australia. | Quang.Ha@uts.edu.au | 37 | 44 | 31 |  |  |  | 176 | 185
148 | 148 | On-line adaptive control of a direct expansion air conditioning system using artificial neural network | Li, N; Xia, L; Deng, SM; Xu, XG; Chan, MY | Li, Ning; Xia, Liang; Deng Shiming; Xu, Xiangguo; Chan, Ming-Yin | 2026-04-29 | 2013 | http://dx.doi.org/10.1016/j.applthermaleng.2013.01.008 | Direct expansion; Air conditioning; On-line; Adaptive control; Artificial neural network; Controllable range | CO | Applied Thermal Engineering | Conventional ANN-based controllers for DX A/C systems, trained off-line, suffer from a limited controllable range — they perform well only near the operating point used for training. Other model-based controllers also struggle with nonlinear, MIMO, and coupled dynamics and lose accuracy when operating conditions drift from the training point. | 1. Develop an ANN-based on-line adaptive controller that updates its dynamic model during operation to capture real-time system performance. 2. Demonstrate that this controller can maintain indoor temperature and humidity within the desired range across the full operating envelope. 3. Validate the controller experimentally on a real DX A/C system. | Subsystem | DX A/C system | Subsystem | Black-Box | Artificial Neural Network (ANN) with time-delay inputs | Model trained on input–output operational data without physical equations. Initial model trained at a single operating point (24 °C DB, 17.1 °C WB, 50% RH). Uses fixed-size recent data window for on-line retraining | No | - | Yes | Lab | N/A | N/A | Lab | Full-scale experimental DX A/C system with: Variable-speed scroll compressor and supply fan, Electronic expansion valve, DX cooling coil in air duct, Controlled indoor chamber (7.6 m × 3.8 m × 2.8 m) with load generating units (heat and moisture) | - | - | - | - | - | - | - | - | - | - | - | Load generating units, Data acquisition system, Customized data logging and control supervisory computer program | 1min | Compressor speed, supply fan speed | Low | Tracking accuracy for dry-bulb and wet-bulb temperatures, Ability to operate across full temperature/humidity range, Disturbance rejection capability | Previous ANN-based controller with off-line trained dynamic model; MIMO controller from Qi & Deng (2009) | Partial | Lab setup | Yes | Model representation limit | HUMIDITY CONTROL; CAPACITY CONTROLLER; A/C UNIT; TEMPERATURE; PERFORMANCE | [Li, Ning; Deng Shiming; Xu, Xiangguo; Chan, Ming-Yin] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China; [Xia, Liang] Univ Nottingham Ningbo China, Dept Architecture & Built Environm, Ningbo 315100, Zhejiang, Peoples R China | Hong Kong Polytechnic University; University of Nottingham Ningbo China | Deng, SM (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | besmd@polyu.edu.hk | 35 | 36 | 53 | 1 |  |  | 96 | 107
149 | 149 | A fast-POD model for simulation and control of indoor thermal environment of buildings | Li, KJ; Su, HY; Chu, J; Xu, C | Li, Kangji; Su, Hongye; Chu, Jian; Xu, Chao | FEB | 2013 | http://dx.doi.org/10.1016/j.buildenv.2012.11.020 | POD; Temperature distribution; FVM; State-space; DMC; Offline-online | CO | Building and Environment | Existing HVAC control methods lack the ability to provide high-resolution, real-time spatial temperature control due to the high computational cost of CFD models. Simplified models (e.g., zonal or empirical) are faster but lose accuracy. There is a need for models that are both accurate and computationally efficient for real-time control. | 1. Develop a fast POD–Galerkin reduced-order model from CFD data to represent indoor temperature distribution dynamics accurately. 2. Integrate the reduced-order model into a Model Predictive Control (MPC) framework for real-time temperature control. 3. Validate the reduced-order model’s accuracy and the controller’s tracking performance via simulation. | Component | Indoor temperature field | Component | White-Box | CFD simulation (Fluent 6.3) of the energy equation in a 2D mid-plane of the room. Finite Volume Method (FVM) discretization. Proper Orthogonal Decomposition (POD) to extract dominant modes. Galerkin projection to obtain reduced-order state-space model. | Fixed airflow field (inlet velocity constant). Homogeneous and constant wall/ceiling/floor temperatures. Neglect radiative heat transfer, phase change, buoyancy coupling (except in separate CFD cases). Ideal temperature sensor; noise modeled as zero-mean white noise in simulations. | No | - | Yes | Simulated data | N/A | MATLAB | Virtual testbed | CFD simulation of a 4 m × 3 m vertical mid-plane of a room with inlet/outlet on west wall; 1200-cell mesh; FVM discretization with turbulent model (k–ε), buoyancy (Boussinesq approximation). | Indoor temperature field | Component | White-Box | CFD solution of the energy equation with fixed inlet velocity; Fluent 6.3 solver. | Fixed airflow, constant surface temperatures, simplified geometry. | No | - | No | None | Fluent | CFD | - | 2s | supply air temperature at inlet | Medium | Tracking accuracy (temperature deviation from reference). Residual temperature difference between reduced-order model and CFD model. Robustness to sensor noise (state estimation accuracy). | CFD model embedded in the same MPC loop. | No | Simulation only | Yes | Model representation limit | PROPER ORTHOGONAL DECOMPOSITION; SYSTEMS; REDUCTION; DESIGN; CFD | [Li, Kangji; Su, Hongye; Chu, Jian; Xu, Chao] Zhejiang Univ, Inst Cyber Syst & Control, Hangzhou 310027, Zhejiang, Peoples R China; [Li, Kangji] Jiangsu Univ, Sch Elect Informat Engn, Zhenjiang 212013, Peoples R China | Zhejiang University; Jiangsu University | Su, HY (corresponding author), Zhejiang Univ, Inst Cyber Syst & Control, Zheda Rd, Hangzhou 310027, Zhejiang, Peoples R China. | lkj@zju.edu.cn; hysu@csc.zju.edu.cn | 56 | 62 | 60 |  |  |  | 150 | 157
150 | 150 | Model Predictive Control for the Operation of Building Cooling Systems | Ma, YD; Borrelli, F; Hencey, B; Coffey, B; Bengea, S; Haves, P | Ma, Yudong; Borrelli, Francesco; Hencey, Brandon; Coffey, Brian; Bengea, Sorin; Haves, Philip | MAY | 2012 | http://dx.doi.org/10.1109/TCST.2011.2124461 | Building energy; building modeling; model predictive control (MPC) | CO | IEEE Transactions on Control Systems Technology | Central cooling plants with thermal storage are often operated suboptimally (e.g., overcharging tanks, inefficient tower/chiller operation). There’s a need for a predictive, constraint-aware controller that uses simplified yet accurate plant/load models, weather/load forecasts, and is feasible for real-time use. | 1. Develop simplified/validated models (chillers+towers power, stratified storage tank, campus load, fan coil). 2. Design a low-complexity, robust MPC (with move-blocking and periodic robust invariant terminal set) to minimize energy cost and improve COP while meeting load/constraints. 3. Implement and experimentally validate MPC on the UC Merced central plant. | Subsystem | TES, Building thermal | Component | Gray-Box | Tank: 4-state stratified switching nonlinear model (charging/discharging) from mass/energy balances; Campus Load: RC building aggregate with solar/internal gains predictors; | A1) Tank is stratified with thin thermocline; minor mixing → 4 states (top/bottom temps & heights). A2) Lower-level loops perfectly track setpoints (no dynamics/tracking error modeled) for tower outlet temp, chilled-water flow, and CHWS temperature. A3) Campus load treated as lumped disturbance. | Yes | Plant power, Fan-coil heat exchange | Yes | Real data | N/A | MATLAB | Real building | UC Merced campus central plant: series chillers + cooling towers + ~7000 m³ thermal storage tank; primary/secondary distribution supplying multiple buildings; experiments S1–S4 over multiple weeks in 2009. | - | - | - | - | - | - | - | - | - | - | - | Automated Logics Web Control (ALC) system | 1h | Tower condenser water supply temperature setpoint, Chilled-water mass flow rate, Chilled-water supply temperature setpoint, Chiller/tower start–stop times | Medium | Daily electricity bill (tariff-weighted energy) and COP of central plant; also qualitative schedule/flow comparisons. | Plant operator baseline (S1) and modified operator policy (S3). MPC compared in S2 and S4. | Yes | Full-scale real-world deployment | Yes | Model representation limit | STORAGE | [Ma, Yudong; Borrelli, Francesco] Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94720 USA; [Hencey, Brandon] Cornell Univ, Sibley Sch Mech & Aerosp Engn, Ithaca, NY 14853 USA; [Coffey, Brian] Univ Calif Berkeley, Dept Architecture, Berkeley, CA 94720 USA; [Bengea, Sorin] United Technol Res Ctr, E Hartford, CT 06108 USA; [Haves, Philip] Univ Calif Berkeley, Lawrence Berkeley Natl Lab, Berkeley, CA 94720 USA | University of California System; University of California Berkeley; Cornell University; University of California System; University of California Berkeley; RTX Corporation; United States Department of Energy (DOE); Lawrence Berkeley National Laboratory; University of California System; University of California Berkeley | Ma, YD (corresponding author), Univ Calif Berkeley, Dept Mech Engn, Berkeley, CA 94720 USA. | myd07@berkeley.edu; fborrelli@berkeley.edu | 319 | 406 | 20 | 3 |  |  | 796 | 803
151 | 151 | Dynamic modeling and control of a direct expansion air conditioning system using artificial neural network | Li, N; Xia, L; Deng, SM; Xu, XG; Chan, MY | Li, Ning; Xia, Liang; Deng Shiming; Xu, Xiangguo; Chan, Ming-Yin | MAR | 2012 | http://dx.doi.org/10.1016/j.apenergy.2011.09.037 | Direct expansion; Air conditioning; Dynamic modeling; Control; Artificial neural network; Variable speed | CO | Applied Energy | Physically based dynamic models for DX A/C systems struggle with strong nonlinear MIMO couplings between indoor temperature and humidity; accurate models to back advanced controllers are hard to build. No prior work was identified applying ANN techniques to simultaneous temperature–humidity control for DX A/C. | 1. Develop an ANN-based dynamic model that maps compressor/fan speeds to indoor dry-bulb & wet-bulb temperatures (explicitly capturing MIMO coupling). 2. Design and experimentally validate an ANN-based controller (direct inverse control) that simultaneously regulates indoor temperature and humidity on a variable-speed DX A/C test rig via compressor and supply-fan speeds. | Subsystem | DX A/C system | Subsystem | Black-Box | Recurrent* multilayer feed-forward ANN (12-30-2), trained with back-propagation and early stopping; inputs include Tdb/Twb and compressor/fan speeds at t, t-1, t-2; output predicts Tdb/Twb at t+1. (*Recurrent via tapped delays on inputs/outputs.) | No outdoor air (OA damper closed); constant condenser airflow (3100 m³/h) at 35 °C; constant superheat 6 °C via EEV; indoor sensible/latent loads held constant during model identification | No | - | Yes | Lab | N/A | N/A | Lab | Full experimental DX A/C system with variable-speed scroll compressor, EEV, plate-fin condenser, louver-fin evaporator used as DX cooling coil in supply duct; variable-speed centrifugal supply fan; closed OA; conditioned space 7.6 m × 3.8 m × 2.8 m with heat & moisture load-generating units; comprehensive sensing and DAQ (“C4”). | - | - | - | - | - | - | - | - | - | - | - | load generating units (LGUs), Platinum resistance temperature sensors, Interfaces for collecting data and outputting control actions | 1min | Compressor speed, supply-fan speed | Low | Setpoint tracking and disturbance rejection of Tdb/Twb; reported ARE/MRE for model validation; steady-state ¦ΔTwb¦ < 0.2 °C after disturbance. | None | Partial | Lab setup | Yes | Model representation limit | HUMIDITY CONTROL; CAPACITY CONTROLLER; CONTROL STRATEGY; HEAT-EXCHANGER; A/C UNIT; TEMPERATURE; PERFORMANCE | [Li, Ning; Xia, Liang; Deng Shiming; Xu, Xiangguo; Chan, Ming-Yin] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Hong Kong, Hong Kong, Peoples R China | Hong Kong Polytechnic University | Deng, SM (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Hong Kong, Hong Kong, Peoples R China. | besmd@polyu.edu.hk | 75 | 79 | 91 | 1 |  |  | 290 | 300
152 | 152 | Model-based robust temperature control for VAV air-conditioning system | Huang, GS; Jordán, F | Huang, Gongsheng; Jordan, Fillip |  | 2012 | http://dx.doi.org/10.1080/10789669.2012.649879 |  | CO | HVAC&R Research | Traditional cascaded PID control in VAV systems suffers from poor robustness against year-round cooling load variations due to fixed outer-loop parameters. Existing advanced controls rarely handle uncertainty, nonlinearity, and constraints simultaneously in HVAC systems. | Develop a model-based robust temperature control for VAV systems capable of year-round application without retuning parameters. Specifically, design a triple-mode control algorithm integrating bilinear feedback control with online cooling load estimation to improve robustness and tracking performance. | Subsystem | Indoor air temperature | Component | White-Box | First-order bilinear thermal model based on energy balance | Zone air is perfectly mixed (single thermal capacitance node). | No | - | No | None | N/A | MATLAB | Virtual testbed | Simulated office unit (single-duct VAV system) with detailed wall and envelope modeling, simplified radiation and convection models, driven by internal and external loads. Surrounded on two sides by façade; other sides connected to rooms with similar conditions. | Building thermal | Component | White-Box | Detailed room model from SIMBAD Building and HVAC Toolbox (thermal envelope, internal gains, radiation, convection). | Central node for zone air temperature. Perfect mixing in the zone. Simplified radiation and convection calculations. | No | - | No | None | SIMBAD | MATLAB | - | 2min | Supply air flow rate | Medium | Average absolute tracking error, Robustness against load variation | Anti-windup PI control (tuned for high load case) | No | Simulation only | No | The process model and testbed are the same | PREDICTIVE CONTROL | [Huang, Gongsheng] City Univ Hong Kong, Div Bldg Sci & Technol, Kowloon, Hong Kong, Peoples R China; [Jordan, Fillip] Czech Tech Univ, Dept Microenvironm & Bldg Serv Engn, CR-16635 Prague, Czech Republic | City University of Hong Kong; Czech Technical University Prague | Huang, GS (corresponding author), City Univ Hong Kong, Div Bldg Sci & Technol, Kowloon, Hong Kong, Peoples R China. | gongsheng.huang@cityu.edu.hk | 9 | 12 | 18 | 3 |  |  | 432 | 445
153 | 153 | Demand reduction in building energy systems based on economic model predictive control | Ma, JR; Qin, J; Salsbury, T; Xu, P | Ma, Jingran; Qin, Joe; Salsbury, Timothy; Xu, Peng | 2026-01-01 | 2012 | http://dx.doi.org/10.1016/j.ces.2011.07.052 | Model predictive control; Demand response; Economics; Energy; Optimization; Simulation | EF | Chemical Engineering Science | Prior DR strategies often used simplified models or open-loop setpoint trajectories that struggled with disturbances (weather, internal loads) and targeted energy/peak reduction rather than cost minimization under TOU + demand charges. The authors note closed-loop implementations with realistic building dynamics and pricing integration were limited. | 1. Develop an economic MPC that minimizes daily energy + demand charges; 2. Build a closed-loop co-simulation (EnergyPlus ↔ MATLAB via BCVTB) for real-time data exchange; 3. Identify ARX models for multi-zone temperature and whole-building power for use in MPC; 4. Compare against baseline and scripted DR strategies and study parameter effects. | Subsystem | Indoor air temperature | Component | Black-Box | 2nd-order MIMO (five zones). | Linear time-invariant ARX identified from PRBS excitation within comfort bounds | Yes | Power use | Yes | Simulated data | System Identification Toolbox | MATLAB | Virtual testbed | EnergyPlus model of a single-story, five-zone commercial building (VAV DX cooling) | Building thermal | Component | White-Box | Detailed simulation in EnergyPlus | Standard EnergyPlus assumptions | Yes | Power use | Yes | Validated platform | BCVTB | EnergyPlus | - | 15min | Zone temperature setpoints | High | Daily energy cost (TOU), demand charge, total cost, energy consumption, peak demand shifting/flattening; weekly savings. | Baseline Night-setup (BL); Linear-up (LU); Step-up (SU) open-loop setpoint strategies. | No | Simulation only | Yes | Model representation limit | THERMAL MASS; STORAGE; TRAJECTORIES; SIMULATION | [Ma, Jingran; Qin, Joe] Univ So Calif, Mork Family Dept Chem Engn & Mat Sci, Los Angeles, CA 90089 USA; [Salsbury, Timothy] Johnson Controls Inc, Milwaukee, WI 53202 USA; [Xu, Peng] Tongji Univ, Sch Mech Engn, Shanghai 200092, Peoples R China | University of Southern California; Johnson Controls Incorporated; Tongji University | Qin, J (corresponding author), Univ So Calif, Mork Family Dept Chem Engn & Mat Sci, 925 Bloom Walk,HED 216, Los Angeles, CA 90089 USA. | jingranm@usc.edu; sqin@usc.edu; tim.i.salsbury@jci.com; xupeng@tongji.edu.cn | 282 | 334 | 67 | 1 |  | SI | 92 | 100
154 | 154 | Model-based optimal control of a dedicated outdoor air-chilled ceiling system using liquid desiccant and membrane-based total heat recovery | Ge, GM; Xiao, F; Xu, XH | Ge, Gaoming; Xiao, Fu; Xu, Xinhua | NOV | 2011 | http://dx.doi.org/10.1016/j.apenergy.2011.04.045 | Dedicated outdoor air system; Chilled ceiling; Liquid desiccant; Membrane-based total heat recovery; Optimal control | CO | Applied Energy | Prior DOAS-CC and liquid-desiccant studies emphasize local control (holding variables at fixed setpoints) rather than optimizing setpoints system-wide under dynamic conditions. There’s limited understanding of whole-system behavior and optimal coordination across components. | 1. Develop simplified yet adaptive models for key components (membrane heat exchanger, liquid desiccant dehumidifier/regenerator, dry cooling coil, chilled ceiling, fans/pumps, building zones). 2. Build a model-based optimal control using a genetic algorithm (GA) to minimize total energy while maintaining indoor temperature and RH comfort. 3. Evaluate performance in a simulated multi-zone office under various conditions vs a conventional fixed-setpoint strategy. | Subsystem | Indoor air temperature, IAQ | Component | Gray-Box | ODE energy & moisture balances with estimated source terms. | Source terms (loads, moisture) are piecewise constant | Yes | Membrane total heat exchanger, Dehumidifier/Regenerator, Dry cooling coil, Chilled ceiling, Fans/Pumps | Yes | Simulated data | N/A | N/A | Virtual testbed | TRNSYS-based multi-zone office (~302 m², 5 zones), perimeter + core. DOAS with membrane total heat exchanger, liquid desiccant (LiCl) dehumidification, dry coil, and chilled ceiling (~50% ceiling coverage in open office). | DOAS-CC system | Subsystem | White-Box | TRNSYS 16 dynamic simulation | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | 1min | Setpoints for (i) DOAS supply-air temperature, (ii) DOAS supply-air humidity ratio, (iii) chilled-ceiling supply-water temperature | Medium | Weighted cost of temperature tracking (JT), RH penalty (JRH), energy (JE); plus reported kWh by end-use and average indoor T/RH, ceiling surface T | Conventional fixed-setpoint strategy | No | Simulation only | Yes | Model representation limit | GENETIC ALGORITHM; CONDITIONING SYSTEM; COOLING SYSTEM; THERMAL-COMFORT; PANEL SYSTEM; PERFORMANCE; ENERGY; DEHUMIDIFICATION; HUMIDITY; OPTIMIZATION | [Ge, Gaoming; Xiao, Fu] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China; [Xu, Xinhua] Huazhong Univ Sci & Technol, Sch Environm Sci & Engn, Dept Bldg Environm & Serv Engn, Wuhan 430074, Peoples R China | Hong Kong Polytechnic University; Huazhong University of Science & Technology | Xiao, F (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | befx@polyu.edu.hk | 63 | 69 | 88 | 11 |  |  | 4180 | 4190
155 | 155 | A novel and dynamic demand-controlled ventilation strategy for CO2 control and energy saving in buildings | Lu, T; Lü, XS; Viljanen, M | Lu, Tao; Lue, Xiaoshu; Viljanen, Martti | SEP | 2011 | http://dx.doi.org/10.1016/j.enbuild.2011.06.005 | Demand-controlled ventilation; Energy saving; Carbon dioxide; Carbon dioxide mass balance equation; Proportional control | CO | Energy and Buildings | Conventional CO₂-based demand-controlled ventilation (DCV) strategies (e.g., proportional, exponential) assume equilibrium (steady-state) CO₂ conditions, which are rarely achieved in practice, leading to over-ventilation and missed energy-saving potential. There is a lack of dynamic, schedule-aware control methods tailored for spaces with well-defined occupied/unoccupied periods | 1. Develop a simple, dynamic CO₂-based DCV strategy that accounts for transient CO₂ dynamics and known occupancy schedules. 2. Evaluate its energy-saving potential against conventional proportional control. 3. Extend applicability to other scheduled or fully occupied buildings. | Subsystem | IAQ | Component | White-Box | First-order CO₂ mass balance ODE | Indoor air is well-mixed (ventilation effectiveness ≈ 100%). Infiltration/exfiltration neglected (supply balanced with return air). Outdoor CO₂ concentration constant. | No | - | No | None | N/A | MATLAB | Virtual testbed | Simulated single-zone sports training center (volume 17,220 m³, 100% outdoor air system) with occupancy schedules and CO₂ generation rates (both simulated and experimentally measured from another gym). | IAQ | Component | White-Box | First-order CO₂ mass balance ODE | Indoor air is well-mixed (ventilation effectiveness ≈ 100%). Infiltration/exfiltration neglected (supply balanced with return air). Outdoor CO₂ concentration constant. | No | - | No | None | N/A | MATLAB | - | 5min | Fresh air damper position | Low | Average CO₂ concentration during occupied hours. Average ventilation rate. Relative energy savings from reduced ventilation. | Conventional proportional control | No | Simulation only | No | The process model and testbed are the same |  | [Lu, Tao; Lue, Xiaoshu; Viljanen, Martti] Aalto Univ, Dept Civil & Struct Engn, Sch Engn, Espoo, Finland | Aalto University | Lu, T (corresponding author), Aalto Univ, Dept Civil & Struct Engn, Sch Engn, Rakentajanaukio 4 A, Espoo, Finland. | tlu@cc.hut.fi | 88 | 102 | 43 | 9 |  |  | 2499 | 2508
156 | 156 | Experimental analysis of model predictive control for an energy efficient building heating system | Siroky, J; Oldewurtel, F; Cigler, J; Prívara, S | Siroky, Jan; Oldewurtel, Frauke; Cigler, Jiri; Privara, Samuel | SEP | 2011 | http://dx.doi.org/10.1016/j.apenergy.2011.03.009 | Building heating system; Energy savings; Model predictive control; Optimization; System identification | CO | Applied Energy | Most reported MPC-for-buildings results were simulation-based or short experiments; there was a need for a detailed, multi-week real-building implementation assessing energy savings and comfort with weather forecasts. | 1. Describe an MPC setup for a radiant heating system; 2. build/identify a tractable dynamic model for control; 3. deploy MPC on a university building; 4. quantify energy savings vs. a conventional heating-curve controller and discuss peak-load effects. | Subsystem | Indoor air temperature | Component | Gray-Box | RC network → linear state-space; parameters via statistical/ML least-squares within an identification procedure | Linear dynamics; constant-flow radiant system; aggregated nodes for rooms/water | No | - | Yes | Real data | Scilab QP/LQ Solver | Scilab | Real building | Multiple 5–8 floor blocks; Crittall-type ceiling radiant system; three-point mixing valve with low-level PID | - | - | - | - | - | - | - | - | - | - | - | RcWare BAS | 20min | Supply-water temperature setpoints for north/south heating circuits | Medium | Energy proxy: sum of (supply − return) water temperature differences (ECM) and ECM normalized by heating degree days (HDD), Thermal comfort | Conventional heating-curve control (baseline) on similar building blocks | Yes | Full-scale real-world deployment | Yes | Model representation limit | STORAGE | [Siroky, Jan] Univ W Bohemia, Fac Sci Appl, Dept Cybernet, Plzen 30614, Czech Republic; [Oldewurtel, Frauke] Swiss Fed Inst Technol Zurich ETHZ, Dept Elect Engn, Automat Control Lab, Zurich, Switzerland; [Cigler, Jiri; Privara, Samuel] Czech Tech Univ, Fac Elect Engn, Dept Control Engn, Prague, Czech Republic | University of West Bohemia Pilsen; Swiss Federal Institutes of Technology Domain; ETH Zurich; Czech Technical University Prague | Siroky, J (corresponding author), Univ W Bohemia, Fac Sci Appl, Dept Cybernet, Univ 8, Plzen 30614, Czech Republic. | jan.siroky@rcware.eu; oldewurtel@control.ee.ethz.ch; jiri.cigler@fel.cvut.cz; samuel.privara@fel.cvut.cz | 577 | 644 | 88 | 9 |  |  | 3079 | 3087
157 | 157 | Nonlinear multivariable control and performance analysis of an air-handling unit | Moradi, H; Saffar-Avval, M; Bakhtiari-Nejad, F | Moradi, Hamed; Saffar-Avval, Majid; Bakhtiari-Nejad, Firooz | APR | 2011 | http://dx.doi.org/10.1016/j.enbuild.2010.11.022 | Air-handling unit; Nonlinear model; Multivariable control; Tracking; Gain scheduling; Feedback linearization | CO | Energy and Buildings | Existing HVAC control strategies (e.g., traditional PI/PID) often underperform across the full operating range of air-handling units (AHUs) due to nonlinearity, coupling between variables, and time-varying characteristics. Many methods fail to balance quick response, robustness, and energy efficiency, especially under varying operating conditions and uncertainties. | 1. Develop and compare two nonlinear model-based control strategies — gain scheduling and feedback linearization — for a nonlinear MIMO AHU model. 2. Evaluate tracking performance, energy use implications, and robustness to parameter uncertainties. 3. Identify advantages/disadvantages of each approach in terms of dynamic response, overshoot, energy consumption, and robustness. | Component | AHU | Component | White-Box | First-principles thermodynamics, heat transfer, and mass transfer equations → formulated as a nonlinear MIMO state-space model. | Ideal gas, complete mixing, homogeneous airflow, negligible zone pressure variation, no leakage except at exhaust valves, fixed outdoor–return air mixing ratio. | No | - | No | None | N/A | N/A | Virtual testbed | Simulated single-zone variable air volume (VAV) AHU with cooling and dehumidification coil, supply/return fans, mixing chamber (25% fresh air), humidifier/dehumidifier. | AHU | Component | White-Box | First-principles thermodynamics, heat transfer, and mass transfer equations → formulated as a nonlinear MIMO state-space model. | Ideal gas, complete mixing, homogeneous airflow, negligible zone pressure variation, no leakage except at exhaust valves, fixed outdoor–return air mixing ratio. | No | - | No | None | N/A | N/A | - | N/A | Valves position of air and cold water flow rates | Low | Tracking performance (rise time ≤ 100 s, overshoot ≤ 10%), Energy proxy: oscillation magnitude in actuator signals (air and water valve positions), Robustness to parameter uncertainties (10% and 20%) | Comparison between gain scheduling and feedback linearization controllers. | No | Simulation only | No | The process model and testbed are the same | CONDITIONING SYSTEM; GENETIC ALGORITHMS; COOLING COIL; HVAC SYSTEM; SIMULATION; MODEL | [Moradi, Hamed; Saffar-Avval, Majid; Bakhtiari-Nejad, Firooz] Amir Kabir Univ Technol, Energy & Control Ctr Excellence, Dept Mech Engn, Tehran, Iran | Amirkabir University of Technology | Moradi, H (corresponding author), Amir Kabir Univ Technol, Energy & Control Ctr Excellence, Dept Mech Engn, Tehran, Iran. | hamedmoradi@mech.sharif.ir | 36 | 45 | 43 | 4 |  |  | 805 | 813
158 | 158 | Model predictive control of a building heating system: The first experience | Prívara, S; Siroky, J; Ferkl, L; Cigler, J | Privara, Samuel; Siroky, Jan; Ferkl, Lukas; Cigler, Jiri | FEB-MAR | 2011 | http://dx.doi.org/10.1016/j.enbuild.2010.10.022 | Optimal control; Subspace identification; Model predictive control; Costs effectiveness | CO | Energy and Buildings | Conventional heating control (on–off, weather-compensated, PID) lacks look-ahead and can’t exploit free gains (e.g., solar) or anticipate weather swings, causing over/under-heating and waste. Most MPC work in HVAC had been simulation-only; robust real-building evidence was missing. | Develop and deploy an MPC for a large university building that 1. uses a building thermal model identified from data and 2. incorporates weather forecasts; compare against a tuned weather-compensated controller and report energy/comfort outcomes. | Subsystem | Indoor air temperature | Subsystem | Black-Box | Linear time-invariant state-space model identified by subspace methods; implemented with Kalman filtering; inputs are forecast outside temperature bounds (T_min, T_max) and heating-water temperature; outputs are T_in and T_rw. | LTI dynamics; stochastic disturbances; states have no physical interpretation | No | - | Yes | Real data | N/A | Scilab | Real building | Eight-floor CTU building using “Crittall” ceiling-radiant heating; control is at building-block level (7 blocks), each with a mixing container and three-port valve driving supply temperature; one reference-room sensor per circuit. | - | - | - | - | - | - | - | - | - | - | - | N/A | N/A | Supply-water temperature setpoint | Medium | Energy consumption, thermal comfort (complaint count), reference-tracking of zone temperature. | Tuned weather-compensated control | Yes | Full-scale real-world deployment | Yes | Model representation limit | DESIGN | [Privara, Samuel; Ferkl, Lukas; Cigler, Jiri] Czech Tech Univ, Fac Elect Engn, Dept Control Engn, Prague 16627 6, Czech Republic; [Siroky, Jan] Univ W Bohemia, Fac Sci Appl, Dept Cybernet, Plzen, Czech Republic | Czech Technical University Prague; University of West Bohemia Pilsen | Prívara, S (corresponding author), Czech Tech Univ, Fac Elect Engn, Dept Control Engn, Tech 2, Prague 16627 6, Czech Republic. | samuel.privara@fel.cvut.cz; jan.siroky@rcware.eu; lukas.ferkl@fel.cvut.cz; jiri.cigler@fel.cvut.cz | 355 | 409 | 43 | 2026-02-03 |  |  | 564 | 572
159 | 159 | Building temperature regulation using a distributed model predictive control | Morosan, PD; Bourdais, R; Dumur, D; Buisson, J | Morosan, Petru-Daniel; Bourdais, Romain; Dumur, Didier; Buisson, Jean | SEP | 2010 | http://dx.doi.org/10.1016/j.enbuild.2010.03.014 | Building heating systems; Distributed model predictive control (dMPC); Energy saving | CO | Energy and Buildings | Conventional room controllers (on/off, P/PI) act independently per zone and ignore thermal coupling, leading to overshoot and poor comfort/energy trade-offs; centralized MPC handles coupling but scales poorly computationally. The paper seeks a scalable alternative that exploits known occupancy to reduce energy without sacrificing comfort. | 1. Propose an MPC cost that weights tracking only during occupied periods to exploit building intermittency. 2. Extend to multizone with coupling and develop a low-overhead distributed MPC (dMPC) with one information exchange per step. 3. Compare decentralized, centralized, and distributed structures in simulation. | Subsystem | Indoor air temperature | Component | Black-Box | ARX (single zone); output-coupled linear state-space with neighbor outputs as exogenous inputs (multizone). | Linearity; well-mixed indoor air; disturbances as zero-mean white noise; inter-zone coupling only via adjacent walls/neighbor outputs. | No | - | Yes | Simulated data | N/A | MATLAB | Virtual testbed | Three zones (3 × 42 m³) with independent 1200 W electric convectors | Building thermal | Component | White-Box | SIMBAD room/building thermal components | Well-mixed zones; coupling through walls | No | - | No | None | SIMBAD | MATLAB | - | 10min | Electrical heating power per zone | Low | Comfort index, Energy index | On/Off, P, PI, decentralized MPC, centralized MPC | No | Simulation only | Yes | Model representation limit | OPTIMIZATION | [Morosan, Petru-Daniel; Bourdais, Romain; Buisson, Jean] SUPELEC IETR, F-35511 Cesson Sevigne, France; [Dumur, Didier] SUPELEC, F-91192 Gif Sur Yvette, France | Universite Paris Saclay; Universite Paris Saclay | Morosan, PD (corresponding author), SUPELEC IETR, Ave Boulaie,BP 81127, F-35511 Cesson Sevigne, France. | petru-daniel.morosan@supelec.fr | 269 | 318 | 42 | 9 |  |  | 1445 | 1452
160 | 160 | Assessment of the controlling envelope of a model-based multivariable controller for vapor compression refrigeration systems | Schurt, LC; Hermes, CJL; Neto, AT | Schurt, Leonardo C.; Hermes, Christian J. L.; Trofino Neto, Alexandre | SEP | 2010 | http://dx.doi.org/10.1016/j.applthermaleng.2010.02.024 | Control; Refrigeration system; Modeling; Experimentation; Controlling envelope | CO | Applied Thermal Engineering | Most prior model-based control work for vapor compression systems identified/validated models only near a single operating point (~±5%), limiting robustness; dual-SISO empirical controllers were confined to neighborhoods of identification. This study asks how far a first-principles, multivariable, model-driven controller can operate away from nominal while maintaining performance. | 1. Build a dynamic, first-principles model (component sub-models) of a variable-speed-compressor + electronic-expansion-valve refrigeration system and linearize it for control design; 2. Design an LQG controller (with Kalman filter + integral action) for simultaneous superheat regulation and cooling-capacity tracking; 3. Experimentally assess reference tracking, disturbance rejection, and the “controlling envelope” (min/max thermal load and superheat ranges) on a lab rig. | Subsystem | HX | Component | White-Box | Heat exchangers: 1-D moving-boundary formulation with mass/energy conservation; two-region (two-phase + single-phase) treatment. Compressor: physics-based relations for mass flow & power; includes heat loss via UA term. Expansion valve: orifice equation with discharge coefficient as power law of subcooling. Internal heat exchanger: ε-NTU style effectiveness relations. Linearization about operating point → state-space for LQG. | 1-D, straight horizontal constant-area coils; negligible diffusion & pressure drop; negligible wall thermal inertia; condenser gas-cooling modeled as saturated region (approximation of similar heat flux); quasi-steady compressor/valve/IHX & secondary loops. | Yes | Compressor, Expansion valve | Yes | Lab | ODE Suite, Refprop | MATLAB | Lab | HFC-134a system with hermetic variable-speed reciprocating compressor (1800–4500 rpm), PWM electronic expansion valve (0–100%), tube-in-tube condenser & evaporator, two secondary loops (water on condenser; 27% ethylene-glycol brine on evaporator), DAQ/controls; extensive instrumentation (Coriolis mass flow, thermocouples, pressure transducers). | - | - | - | - | - | - | - | - | - | - | - | Coriolis mass flow meter, Immersion T-type thermocouples, Pressure transducers, Turbine flow meter, Wattmeter, Control and Data Acquisition System | 2s | Compressor speed, EEV opening | Low | Reference-tracking accuracy/undershoot, disturbance rejection to secondary-flow perturbations, and achievable operating envelope in terms of (i) thermal load range and (ii) superheat range without instability; model-to-experiment error for pressures/power | None | Partial | Lab setup | Yes | Model representation limit | PERFORMANCE; CYCLES | [Schurt, Leonardo C.; Hermes, Christian J. L.] Univ Fed Santa Catarina, POLO Res Labs Emerging Technol Cooling & Thermoph, BR-88040900 Florianopolis, SC, Brazil; [Trofino Neto, Alexandre] Univ Fed Santa Catarina, Dept Automat & Syst Engn, BR-88040900 Florianopolis, SC, Brazil | Universidade Federal de Santa Catarina (UFSC); Universidade Federal de Santa Catarina (UFSC) | Hermes, CJL (corresponding author), Univ Fed Parana, Dept Mech Engn, POB 19011, BR-81531990 Curitiba, Parana, Brazil. | chermes@ufpr.br | 26 | 36 | 30 | 13 |  |  | 1538 | 1546
161 | 161 | Dynamic Model-Based Fault Tolerant Control of Variable Air Volume Air Conditioning System | Talukdar, A; Patra, A | Talukdar, Atanu; Patra, Amit | MAR | 2010 | http://dx.doi.org/10.1080/10789669.2010.10390902 |  | CO | HVAC&R Research | Most existing FDD methods for Variable Air Volume Air Conditioning (VAVAC) systems are data-driven (e.g., ANN, fuzzy logic, PCA) and often do not use first-principles dynamic models. There is a lack of model-based approaches that can detect, isolate, and tolerate stuck actuator (damper vane) faults while maintaining control performance. | 1. Develop a dynamic model-based fault tolerant control method for a VAVAC system. 2. Apply an Adaptive Interactive Multiple Observer (AIMO) scheme for detecting, isolating, and estimating single and multiple stuck damper faults. 3. Use fault information to reconfigure control and maintain zone temperature setpoints. | Subsystem | VAV system | Subsystem | White-Box | Lumped-parameter, first-principles state-space model derived from conservation of mass and energy (based on Thosar et al. 2008). | Constant heat transfer coefficients. Lumped air masses in zones and coil. | No | - | No | None | N/A | N/A | Virtual testbed | Simulated two-zone VAVAC system with redundant VAV boxes, faults injected by fixing damper vane positions at constant values | VAV system | Subsystem | White-Box | Lumped-parameter, first-principles state-space model derived from conservation of mass and energy (based on Thosar et al. 2008). | Constant heat transfer coefficients. Lumped air masses in zones and coil. | No | - | No | None | N/A | N/A | - | 75 s (for single fault isolation) and 10 s (for double fault decision) | Damper vane positions | Low | Fault detection and isolation correctness. Ability to restore zone temperature to setpoint after fault. Estimated stuck damper flow rate accuracy. | Nominal control (no FTC) | No | Simulation only | No | The process model and testbed are the same | DIAGNOSIS | [Talukdar, Atanu; Patra, Amit] Indian Inst Technol, Dept Elect Engn, Kharagpur 721302, W Bengal, India | Indian Institute of Technology System (IIT System); Indian Institute of Technology (IIT) - Kharagpur | Talukdar, A (corresponding author), Indian Inst Technol, Dept Elect Engn, Kharagpur 721302, W Bengal, India. |  | 17 | 17 | 16 | 2 |  |  | 233 | 254
162 | 162 | A model-driven multivariable controller for vapor compression refrigeration systems | Schurt, LC; Hermes, CJL; Neto, AT | Schurt, Leonardo C.; Hermes, Christian J. L.; Trofino Neto, Alexandre | NOV | 2009 | http://dx.doi.org/10.1016/j.ijrefrig.2009.04.004 | Refrigerating system; Compression system; Modeling; Simulation; Control; Comparison; Experiment | CO | International Journal of Refrigeration | Prior control strategies for variable-speed compressor (VSC) + electronic expansion valve (EEV) either used empirical, narrow-range identifications (valid only near an operating point) or validated models only within ~5% around that point. There was a need for a first-principles dynamic model validated over a broad operating range and usable to design a multivariable controller. | 1. Develop a first-principles dynamic simulation model for a vapor-compression system; 2. validate it over a wide range (≈ ±30%); 3. design a model-driven MIMO controller (LQG with Kalman observer) for evaporator superheat and cooling-capacity regulation via compressor speed and valve opening; 4. evaluate tracking and disturbance-rejection on a lab breadboard rig. | Subsystem | HX | Component | White-Box | Moving-boundary 1-D conservation (mass & energy) for HX with time-varying phase boundary. ε–NTU thermal model for each HX region. Compressor: map/isentropic relations + energy balance for discharge enthalpy. EEV: orifice equation with subcooling-dependent discharge coefficient. Internal HX: steady energy balance/effectiveness. | 1-D, straight horizontal serpentine; negligible axial diffusion; negligible pressure drop; negligible wall thermal inertia; condenser gas-cooling region treated as saturated (two-phase-equivalent heat flux). Mean void fraction fitted (~0.8). Compressor/valve treated quasi-steadily. | Yes | Compressor, Expansion valve | Yes | Lab | ODE Suite, Refprop | MATLAB | Lab | HFC-134a rig with hermetic reciprocating VSC (1800–4500 rpm), PWM EEV (1–99%), tube-in-tube evaporator & condenser, two secondary loops (27% ethylene-glycol brine for evaporator; water for condenser); Coriolis mass flow meter, turbine flow meters, type-T thermocouples, pressure transducers; DAQ controls compressor speed & EEV opening. | - | - | - | - | - | - | - | - | - | - | - | Coriolis mass flow meter, Immersion T-type thermocouples, Pressure transducers, Turbine flow meter, Wattmeter, Control and Data Acquisition System | 2s | Compressor speed, EEV opening | Low | Reference-tracking accuracy; disturbance rejection under ~15% thermal-load increase; model-to-experiment pressure errors within ≲2% (ID) and ≲5% (validation) and good dynamic trend matching. | None | Partial | Lab setup | Yes | Model representation limit | EXPANSION; PERFORMANCE | [Hermes, Christian J. L.] Univ Fed Santa Catarina, POLO Natl Inst Sci & Technol Refrigerat & Thermop, BR-88040900 Florianopolis, SC, Brazil; [Schurt, Leonardo C.; Trofino Neto, Alexandre] Univ Fed Santa Catarina, Dept Automat & Syst Engn, BR-88040900 Florianopolis, SC, Brazil | Universidade Federal de Santa Catarina (UFSC); Universidade Federal de Santa Catarina (UFSC) | Hermes, CJL (corresponding author), Univ Fed Santa Catarina, POLO Natl Inst Sci & Technol Refrigerat & Thermop, BR-88040900 Florianopolis, SC, Brazil. | hermes@polo.ufsc.br | 71 | 81 | 32 | 7 |  |  | 1672 | 1682
163 | 163 | A robust model predictive control strategy for improving the control performance of air-conditioning systems | Huang, GS; Wang, SW; Xu, XH | Huang, Gongsheng; Wang, Shengwei; Xu, Xinhua | OCT | 2009 | http://dx.doi.org/10.1016/j.enconman.2009.06.014 | Time-delay uncertainty; Robust model predictive control; Air-conditioning system; Robustness | CO | Energy Conversion and Management | Classical PI/PID and robust H∞ controllers struggle with (i) time-varying dynamics, (ii) uncertainties (notably time delay and process gain), and (iii) actuator constraints; prior MPC in HVAC handled constraints but not model uncertainty. | Propose a robust MPC for AHU supply-air temperature that (a) explicitly models uncertain time delay and gain via an uncertainty polytope, (b) uses an offline LMI-based design yielding a piecewise state-feedback law, and (c) demonstrates improved tracking and disturbance rejection vs. PI in a dynamic VAV simulation. | Subsystem | AHU | Component | Black-Box | First-order plus time delay with parametric uncertainty | Time constant T treated nominal (uncertainty neglected relative to K,τ). | No | - | No | None | N/A | N/A | Virtual testbed | Dynamic simulation of VAV AHU + building | VAV system | Subsystem | White-Box | First-order building thermal network; nonlinear coil models; actuator/sensor time-constant models; empirical damper/valve characteristics. | N/A | No | - | Yes | Validated platform | N/A | N/A | - | 15s | Cooling-coil valve | Low | Tracking (settling time to step changes 13→16 °C and back). Disturbance rejection quantified by AIAE (average integrated absolute error). Constraint satisfaction | Conventional PI (Ziegler–Nichols tuned) | No | Simulation only | Yes | Model representation limit | TEMPERATURE CONTROL; HEATING-SYSTEMS; VENTILATION | [Xu, Xinhua] Huazhong Univ Sci & Technol, Dept Bldg Environm & Serv Engn, Sch Environm Sci & Engn, Wuhan 430074, Hubei, Peoples R China; [Huang, Gongsheng; Wang, Shengwei; Xu, Xinhua] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China | Huazhong University of Science & Technology; Hong Kong Polytechnic University | Xu, XH (corresponding author), Huazhong Univ Sci & Technol, Dept Bldg Environm & Serv Engn, Sch Environm Sci & Engn, Wuhan 430074, Hubei, Peoples R China. | bexhxu@hust.edu.cn | 67 | 74 | 50 | 10 |  |  | 2650 | 2658
164 | 164 | Optimal control strategy for a multi-zone air conditioning system using a genetic algorithm | Mossolly, M; Ghali, K; Ghaddar, N | Mossolly, M.; Ghali, K.; Ghaddar, N. | JAN | 2009 | http://dx.doi.org/10.1016/j.energy.2008.10.001 | Control of HVAC system; Energy saving; Optimal control strategy; Model based optimization; Genetic algorithm | CO | Energy | Conventional VAV control keeps a fixed supply-air temperature and fixed (peak-sized) ventilation, which wastes energy and can violate IAQ during low-flow periods. There’s a need for system-level, multi-variable, model-based strategies that maintain comfort and IAQ while reducing energy. | 1. Formulate and solve multi-objective optimal control problems for a multi-zone VAV system using a genetic algorithm (GA); 2. Compare a conventional strategy with two advanced strategies: (a) track zone temperature + IAQ by optimizing SAT and fresh-air rate; (b) track PMV + IAQ by optimizing SAT, supply flow, and fresh-air; 3. Quantify energy/comfort/IAQ tradeoffs over daily operation and a 4-month summer season. | Whole System | Building thermal, IAQ | Component | White-Box | Lumped thermal network (single capacitance per wall/roof), well-mixed zone air energy balance, CO₂ and moisture mass balances | Each zone air is well mixed; Walls/roof as single lumped-capacitance nodes; Air capacitance neglected; No interzone air infiltration; | Yes | Mixing box, VAV retun duct, Energy use | Yes | Simulated data | N/A | MATLAB | Virtual testbed | Seven-zone academic floor (library, computer lab, teacher’s room, lecture hall, three classrooms) served by chiller, chilled-water coil, reheat, supply/return fans, VAV boxes, mixing box | Building thermal, IAQ | Component | White-Box | Lumped thermal network (single capacitance per wall/roof), well-mixed zone air energy balance, CO₂ and moisture mass balances | Each zone air is well mixed; Walls/roof as single lumped-capacitance nodes; Air capacitance neglected; No interzone air infiltration; | Yes | Mixing box, VAV retun duct, Energy use | Yes | Simulated data | N/A | MATLAB | - | N/A | Set points for SAT, fresh-air fraction/flow, zone supply flows | Medium | Energy cost, Thermal comfort, IAQ | Conventional fixed-SAT/fixed-ventilation strategy | No | Simulation only | No | The process model and testbed are the same | DEMAND-CONTROLLED VENTILATION; HVAC; OPTIMIZATION; DESIGN | [Mossolly, M.; Ghaddar, N.] Amer Univ Beirut, Fac Engn & Architecture, Dept Mech Engn, Beirut 11072020, Lebanon; [Ghali, K.] Beirut Arab Univ, Beirut, Lebanon | American University of Beirut; Beirut Arab University | Ghaddar, N (corresponding author), Amer Univ Beirut, Fac Engn & Architecture, Dept Mech Engn, POB 11-236,Riad El Solh, Beirut 11072020, Lebanon. | farah@aub.edu.lb | 212 | 260 | 34 | 1 |  |  | 58 | 66
165 | 165 | A model-based optimal ventilation control strategy of multi-zone VAV air-conditioning systems | Xu, XH; Wang, SW; Sun, ZW; Xiao, F | Xu, Xinhua; Wang, Shengwei; Sun, Zhongwei; Xiao, Fu | JAN | 2009 | http://dx.doi.org/10.1016/j.applthermaleng.2008.02.017 | Model-based control; Multi-zone ventilation; Optimal temperature reset; Critical zone ventilation; Demand-controlled ventilation | CO | Applied Thermal Engineering | CO₂-based DCV works in single-zone systems but leads to over-/under-ventilation across zones in multi-zone VAV systems because each zone’s required outdoor-air fraction differs with occupancy and load. Prior multi-zone DCV approaches either risk IAQ issues at low occupancy or use non-optimal temperature resets. The field lacks a method that (i) accounts for unvitiated (unused) fresh air from over-ventilated zones and (ii) optimally resets critical-zone temperature setpoints while balancing comfort, IAQ, and energy. | Propose and evaluate a model-based optimal ventilation control strategy for multi-zone VAV systems, combining: 1. dynamic multi-zone ventilation equation that corrects total outdoor-air intake by counting unvitiated fresh air; and 2. dynamic temperature setpoint reset for the critical zone, optimized by GA using dynamic simplified models to jointly minimize energy, comfort (PMV/PPD), and IAQ (CO₂). | Subsystem | Indoor air temperature, IAQ | Component | Gray-Box | Zone energy/moisture/CO₂ balances | Within each prediction period: source terms (sensible/latent/CO₂) and identified parameters are quasi-constant; return-air conditions treated as constant; VAV loop delay neglected | Yes | Coil, Fan | Yes | Simulated data | N/A | N/A | Virtual testbed | Detailed dynamic TRNSYS model of an office half-floor with 8 zones served by a single AHU with VAV boxes | VAV system, IAQ | Subsystem | White-Box | TRNSYS components | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | 1min | Critical-zone temperature setpoint, OA setpoint | High, Medium | PPD/PMV; IAQ; Energy | (i) Conventional DCV (uses total occupancy only) and (ii) Multi-zone DCV (dynamic ventilation equation only) | No | Simulation only | Yes | Model representation limit | CO2-BASED OCCUPANCY DETECTION; GENETIC ALGORITHM; ENERGY; VALIDATION; NETWORK; FLOW | [Xu, Xinhua; Wang, Shengwei; Sun, Zhongwei; Xiao, Fu] Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China | Hong Kong Polytechnic University | Wang, SW (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | beswwang@polyu.edu.hk | 92 | 106 | 29 | 1 |  |  | 91 | 104
166 | 166 | Model-based demand-limiting control of building thermal mass | Lee, KH; Braun, JE | Lee, Kyoung-ho; Braun, James E. | OCT | 2008 | http://dx.doi.org/10.1016/j.buildenv.2007.10.009 | Building thermal mass; Demand-limiting control; Model-based control; Commercial buildings | EF | Building and Environment | Prior work showed that adjusting zone temperature setpoints can shift load and reduce peaks, but there was no general, building-specific method to compute setpoint trajectories that minimize peak electrical/cooling demand. | 1. Develop a model-based demand-limiting (DL) strategy that uses an inverse (gray-box) building model trained on field data to generate setpoint trajectories that cap peak cooling below a target; 2. Demonstrate and evaluate the approach on a small-commercial-like facility (Iowa Energy Center’s ERS) including simulation and field tests, with peak-load reduction and comfort assessment. | Subsystem | Building thermal | Component | Gray-Box | 2R2C layers per envelope element (external wall, internal wall, roof/ceiling, floor) in a state-space RC network; converted to a time-series transfer function for hourly loads | All test rooms lumped into one thermal zone; solar through windows absorbed on floor; internal radiative gains distributed to walls/floor only; no infiltration or night-sky radiation; adjacent occupied areas at same temperature as test zone; ground temperature constant (≈17.5 °C); lighting 90% radiative/10% convective, simulated plug/people gains 5% radiative/95% convective; linear setpoint change within an hour. | No | - | Yes | Real data | N/A | N/A | Real building | Iowa Energy Center Energy Resource Station, ERS. Eight test rooms (east/west/south/exterior + interior), ~25.6 m² each, 2.59 m height; heavyweight envelope but limited thermal connection to zone air | - | - | - | - | - | - | - | - | - | - | - | Sensors: Platinum 1000Ω RTD probe, Flow ring, Differential pressure sensor; Local weather station (T/RH, wind, solar, pressure) | 1h | Zone air temperature setpoint trajectory | High | Peak Load Ratio (PLR) vs. baseline; peak cooling demand reduction during DL period; comfort survey (AM/PM). | Night-setup (NS) control | Yes | Full-scale real-world deployment | Yes | Model representation limit |  | [Braun, James E.] Purdue Univ, Sch Mech Engn, W Lafayette, IN 47907 USA; [Lee, Kyoung-ho] Korea Elect Power Corp, Korea Elect Power Res Inst, Taejon 305380, South Korea | Purdue University System; Purdue University; Purdue University in Indianapolis; Korea Electric Power Corporation (KEPCO) | Braun, JE (corresponding author), Purdue Univ, Sch Mech Engn, 140 S Intramural Dr, W Lafayette, IN 47907 USA. | jbraun@purdue.edu | 123 | 146 | 43 | 10 |  |  | 1633 | 1646
167 | 167 | Model-based fault detection and diagnosis of HVAC systems using support vector machine method | Liang, J; Du, R | Liang, J.; Du, R. | SEP | 2007 | http://dx.doi.org/10.1016/j.ijrefrig.2006.12.012 | air conditioning; process; detection; anomaly; maintenance | FDD | International Journal of Refrigeration | 1. Existing FDD methods for HVAC often require large amounts of measurement data under varied operating conditions, rely heavily on numerous accurate sensors, and may not be cost-effective. 2. Many applications are still in the laboratory stage and focus on vapor compression systems, with limited research on broader HVAC subsystems. | 1. Propose a Model-Based Fault Detection and Diagnosis (MBFDD) method combining a physics-based lumped-parameter model with a Support Vector Machine (SVM) classifier. 2. Identify fault-sensitive variables for detection and diagnosis of common HVAC faults (recirculation damper stuck, cooling coil fouling/block, supply fan speed decreasing). 3. Evaluate the method’s efficiency, accuracy, and cost-effectiveness through simulation. | Whole System | AHU, Indoor air temperature | Subsystem | White-Box | Lumped-parameter physical model based on mass and energy balance equations. Cooling mode only; constant inlet chilled water temperature; fixed damper positions and fan speeds. | Lumped-parameter simplification to reduce complexity. White, zero-mean, uncorrelated Gaussian noise for sensors. | Yes | Chiller | No | None | N/A | N/A | Virtual testbed | Simulation of a single-zone HVAC system with a chiller, air handling unit, ductwork, and control system, subject to ambient temperature, humidity, and internal load disturbances. | AHU, Indoor air temperature | Subsystem | White-Box | Lumped-parameter physical model based on mass and energy balance equations. Cooling mode only; constant inlet chilled water temperature; fixed damper positions and fan speeds. | Lumped-parameter simplification to reduce complexity. White, zero-mean, uncorrelated Gaussian noise for sensors. | Yes | Chiller | No | None | N/A | N/A | - | N/A | - | - | Fault detection sensitivity vs. false alarm rate (via threshold tuning), Fault diagnosis accuracy | None | No | Simulation only | No | The process model and testbed are the same | AIR-HANDLING UNIT; AHU | Chinese Univ Hong Kong, Dept Automat & Comp Aided Engn, Shatin, Hong Kong, Peoples R China | Chinese University of Hong Kong | Liang, J (corresponding author), Chinese Univ Hong Kong, Dept Automat & Comp Aided Engn, Room 110 MMW, Shatin, Hong Kong, Peoples R China. | jliang@acae.cuhk.edu.hk | 174 | 205 | 30 | 6 |  |  | 1104 | 1114
168 | 168 | A vapour compression chiller fault detection technique based on adaptative algorithms.: Application to on-line refrigerant leakage detection | Navarro-Esbrí, J; Torrella, E; Cabello, R | Navarro-Esbri, J.; Torrella, E.; Cabello, R. | AUG | 2006 | http://dx.doi.org/10.1016/j.ijrefrig.2005.12.008 | chiller; compression system; process; detection; leak; fault; failure | FDD | International Journal of Refrigeration | 1. Existing FDD methods for vapour compression chillers often rely on steady-state models or model-free approaches with limited sensitivity to incipient faults and poor robustness to transient conditions. 2. Many physical models require extensive, hard-to-obtain data, making them unsuitable for online use. 3. There is a need for an automated, adaptive, low-data-requirement method that works in both steady-state and transient operation, detects faults quickly, and avoids false alarms. | 1. Propose a robust, adaptive dynamic black-box model–based FDD technique for vapour compression chillers. 2. Enable online refrigerant leakage detection with high sensitivity, minimal detection delay, and robustness against load variation–induced false alarms. 3. Validate the method experimentally in a lab chiller setup under faulty and fault-free conditions. | Component | Chiller | Component | Black-Box | Multi-regressive exogenous (MR) model with Kalman filter for parameter adaptation | Chiller behavior can be captured using a linear MR structure relating suction pressure to recent input histories. Selected inputs sufficiently represent operating conditions affecting the output variable. Gaussian noise processes for system and measurement noise in Kalman filter formulation. | No | - | Yes | Lab | N/A | N/A | Lab | Liquid-to-liquid vapour compression chiller in lab facility. Includes compressor, condenser, thermostatic expansion valve, evaporator, water/glycol secondary loops with controlled load and condenser conditions. | - | - | - | - | - | - | - | - | - | - | - | LABVIEW, National Instruments PC-based data acquisition system, Sensors: 14 K-type thermocouples, Piezoelectric pressure transducers, Coriolis-effect mass flow meter, Electromagnetic flow meter, Capacitive sensor, Digital Wattmeter | 0.01s | - | - | Detection sensitivity, Detection delay (near-zero delay; only limited by sampling period), Robustness to false alarms under load changes | None | Partial | Lab setup | Yes | Model representation limit | LIQUID CHILLERS; PERFORMANCE; DIAGNOSIS; MODELS | Univ Jaume 1, Dept Mech Engn & Construct, E-12071 Castellon, Spain; Univ Politecn Valencia, Dept Appl Thermodynam, E-46022 Valencia, Spain | Universitat Jaume I; Universitat Politecnica de Valencia | Navarro-Esbrí, J (corresponding author), Univ Jaume 1, Dept Mech Engn & Construct, Campus Riu Sec, E-12071 Castellon, Spain. | navarroj@emc.uji.es | 33 | 39 | 29 | 5 |  |  | 716 | 723
169 | 169 | Dynamic simulation of energy management control functions for HVAC systems in buildings | Huang, WZ; Zaheeruddin, M; Cho, SH | Huang, WZ; Zaheeruddin, M; Cho, SH | MAY | 2006 | http://dx.doi.org/10.1016/j.enconman.2005.06.011 | energy management control systems; HVAC systems; adaptive control; optimization; building operation; energy savings | CO | Energy Conversion and Management | 1. Existing EMC (Energy Management Control) functions in HVAC systems are mostly heuristic and empirical, with limited verification of their effectiveness for energy efficiency. 2. Past studies often implemented only one EMC function at a time, rarely integrating multiple functions into one system. 3. Advanced optimization and control methods (like MPC) exist but are too complex and unproven for easy integration into existing commercial EMC systems. | 1. Develop and integrate five EMC functions (OA economizer cycle, programmed start lead time, programmed stop lead time, load reset, occupied time adaptive control) into one system. 2. Use a single-zone VAV-HVAC dynamic model as the simulation platform to evaluate the functions. 3. Propose a steady-state optimization method to compute optimal set points for improved energy efficiency. | Whole System | Indoor air temperature, HX, TES | Component | White-Box | Energy balance equations for zone, transient cooling coil model (counter-cross flow), heat pump/storage tank energy balance | Neglected duct heat gains. | Yes | Heat pump, Fan | No | None | N/A | N/A | Virtual testbed | Simulated single-zone VAV-HVAC system including zone, cooling coil, heat pump, storage tank, and fan, operated under various EMC strategies. | Indoor air temperature, HX, TES | Component | White-Box | Energy balance equations for zone, transient cooling coil model (counter-cross flow), heat pump/storage tank energy balance | Neglected duct heat gains. | Yes | Heat pump, Fan | No | None | N/A | N/A | - | 30min | Supply air mass flow rate, Supply water mass flow rate, Heat pump energy input | Medium | Daily energy consumption (MJ), percentage energy savings. | 1. Base case (duty cycle during occupied time + on/off OA damper control during unoccupied time). 2. EMC without optimization. | No | Simulation only | No | The process model and testbed are the same | VAV SYSTEMS | Concordia Univ, Montreal, PQ, Canada; Jeonju Univ, Mech & Automat Engn Dept, Jeonju 520759, Jellabukdo, South Korea | Concordia University - Canada; Jeonju University | Concordia Univ, Montreal, PQ, Canada. | zaheer@bcee.concordia.ca | 95 | 111 | 47 | 2026-07-08 |  |  | 926 | 943
170 | 170 | Online fault detection and diagnosis in VAV air handling unit by RARX modeling | Yoshida, H; Kumar, S; Morita, Y | Yoshida, H; Kumar, S; Morita, Y | APR | 2001 | http://dx.doi.org/10.1016/S0378-7788(00)00121-3 | commercial buildings; equipment; field; online FDD; RARX commercial buildings; RARX modeling | FDD | Energy and Buildings | Most building management systems (BMS) lack automatic and cost-effective FDD tools for HVAC systems, especially for variable air volume (VAV) subsystems under real operating conditions. Prior work often relied on simulated data, which may not represent real operational dynamics and interactions, and required expensive sensing setups. | Develop and validate a dynamic, online, and computationally efficient model-based FDD method for VAV AHUs using a recursive autoregressive exogenous (RARX) model, tested under real building conditions with artificially introduced faults. Propose both a frequency-response–based method and a simpler behavior-comparison method for multiple VAV systems. | Subsystem | VAV system | Subsystem | Black-Box | Recursive AutoRegressive with eXogenous input (RARX) model with forgetting factor | Treats each VAV subsystem as SISO system with temperature deviation as input and change in airflow as output. Assumes system is stable during detection period | No | - | Yes | Real data | N/A | N/A | Historical data | Real building operation data with controlled, documented faults introduced physically. | - | - | - | - | - | - | - | - | - | - | - | - | 1h | - | - | Ability to detect and diagnose faults (threshold-based classification of NAR values), Robustness against sensor bias errors, False alarm rates under various thresholds | Simpler behavior-comparison method vs. frequency-response method | No | Historical data | Yes | Model representation limit | ARX | Kyoto Univ, Fac Engn, Dept Global Environm Engn, Sakyo Ku, Kyoto 60601, Japan | Kyoto University | Yoshida, H (corresponding author), Kyoto Univ, Fac Engn, Dept Global Environm Engn, Sakyo Ku, Kyoto 60601, Japan. |  | 47 | 54 | 33 | 4 |  | SI | 391 | 401
171 | 171 | Adaptive control of multivariable thermal processes in HVAC systems | Singh, G; Zaheer-uddin, M; Patel, RV | Singh, G; Zaheer-uddin, M; Patel, RV | OCT | 2000 | http://dx.doi.org/10.1016/S0196-8904(99)00182-X | adaptive control; HVAC processes; multivariable control; temperature control; space heating | CO | Energy Conversion and Management | Previous adaptive control applications in HVAC mainly targeted single-input, single-output processes, lacking treatment of multivariable, nonlinear, multi-zone systems under realistic disturbances and parameter variations. Also, existing methods often require steady-state conditions or repeated open-loop tests, which are impractical for HVAC operation. | 1. Develop a robust adaptive controller for a multi-input, multi-output nonlinear fan-coil heating (FCH) system. 2. Achieve regulation of zone and boiler temperatures under static (e.g., outdoor temperature) and dynamic (e.g., solar gains, thermal inertia) disturbances. 3. Ensure continuous adaptation to parameter changes and unmodeled dynamics. 4. Validate robustness against parameter variations and actuator nonlinearities | Subsystem | Indoor air temperature, Boiler | Component | White-Box | Physics-based bilinear energy balance equations for thermal dynamics, plus 5th-order linear disturbance model for wall heat storage | Heat transfer coefficients and loss coefficients are constant. Linearized around operating points for controller design. | No | - | No | None | N/A | N/A | Virtual testbed | Simulated two-zone FCH system with nonlinear physics, dynamic disturbances from thermal mass and solar gains. | Indoor air temperature, Boiler | Component | White-Box | Physics-based bilinear energy balance equations for thermal dynamics, plus 5th-order linear disturbance model for wall heat storage | Heat transfer coefficients and loss coefficients are constant. Linearized around operating points for controller design. | No | - | No | None | N/A | N/A | - | N/A | Normalized mass flow rate of hot water to fan-coil units in two zones, Normalized energy input to boiler | Medium | Tracking error (temperature regulation to setpoints). Disturbance rejection time. Maximum overshoot (%). Robustness to parameter variation and unmodeled dynamics. | Fixed-gain controller with same control structure | No | Simulation only | No | The process model and testbed are the same |  | Concordia Univ, Montreal, PQ H3G 1M8, Canada | Concordia University - Canada | Zaheer-uddin, M (corresponding author), Concordia Univ, 1455 de Maisonneuve Blvd W, Montreal, PQ H3G 1M8, Canada. |  | 8 | 14 | 41 | 15 |  |  | 1671 | 1685
172 | 172 | Model-based optimal control of VAV air-conditioning system using genetic algorithm | Wang, SW; Jin, XQ | Wang, SW; Jin, XQ | AUG | 2000 | http://dx.doi.org/10.1016/S0360-1323(99)00032-3 |  | CO | Building and Environment | Prior system-level HVAC optimization relied on simplified static/dynamic equations or detailed physical models that were impractical for online control; data-driven black-box models could be unreliable outside training ranges. There was a need for an online, system-level optimizer with accurate-yet-tractable dynamic models and robust search. | 1. Develop an online supervisory optimal control for VAV systems that jointly optimizes multiple setpoints (AHU supply air temperature, outdoor ventilation flow, chilled-water supply temperature) using model-based prediction + genetic algorithm. 2. Build incremental, self-tuning (adaptive) physical dynamic models for key subsystems to predict comfort, IAQ (CO₂, VOC), humidity, ventilation adequacy, and energy. | Whole System | Indoor air temperature, IAQ | Component | Gray-Box | Incremental finite-time prediction models of zones (temperature/humidity), IAQ mass balance | Lumped-parameter | Yes | Coil, Fan/Pump, Chiller | Yes | Simulated data | N/A | N/A | Virtual testbed | TRNSYS simulation of a centralized VAV A/C system serving an 1166 m² floor with 8 zones (VAV & some CAV), two AHUs, supply/return fans, chilled-water loop | HVAC system | Whole System | White-Box | TRNSYS component-level modeling of HVAC and building envelope. | Standard TRNSYS modeling | No | - | Yes | Validated platform | N/A | TRNSYS | - | 1min | AHU supply air temperature setpoint; Outdoor air ventilation rate setpoint; Chilled-water supply temperature setpoint. | Medium | PMV/PPD, IAQ, Energy | Conventional strategy with constant setpoints | No | Simulation only | Yes | Model representation limit |  | Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China | Hong Kong Polytechnic University | Wang, SW (corresponding author), Hong Kong Polytech Univ, Dept Bldg Serv Engn, Kowloon, Hong Kong, Peoples R China. | beswwang@polyu.edu.hk | 215 | 280 | 35 | 6 |  |  | 471 | 487
173 | 173 | How far back shall we peer? Optimal air handling unit control leveraging extensive past observations | Rui Li, Zhengbo Zou | Rui Li, Zhengbo Zou | FEB | 2025 | https://doi.org/10.1016/j.buildenv.2024.112347 | Learning-based control, HVAC optimization, Thermal comfort, Time-series modeling | CO | Building and Environment | RL for HVAC control is promising but hampered by sample inefficiency and sub-optimal convergence; moreover, how much historical context an RL agent should use in non-Markovian HVAC settings is unclear. | 1. Build a data-driven RL environment model for an AHU using a Transformer variant (Informer) that leverages long history; 2. Quantify how varying look-back lengths affect both modeling accuracy and RL control performance; 3. Demonstrate energy and comfort benefits vs rule-based feedback control (RBFC). | Subsystem | AHU | Component | Black-Box | Transformer (vanilla) and Informer (ProbSparse attention + distillation) compared to Bi-LSTM; Informer used for RL environment. | Relies on BAS data after preprocessing (missing data imputation, outlier removal, min–max scaling, collinearity filtering) | No | - | Yes | Real data | N/A | N/A | Virtual testbed | AHU from an academic building (BAS data 2018-07 to 2023-10, 10-min resolution) | AHU | Component | Black-Box | Transformer (vanilla) and Informer (ProbSparse attention + distillation) compared to Bi-LSTM; Informer used for RL environment. | Relies on BAS data after preprocessing (missing data imputation, outlier removal, min–max scaling, collinearity filtering) | No | - | Yes | Real data | N/A | N/A | - | 10min | HRV supply fan power, mixed air temperature setpoint, supply airflow, supply air temperature setpoint, VFD speed. | Medium, Low | Electricity and PPD | Rule-Based Feedback Control (RBFC); Environment-model baselines (Bi-LSTM, vanilla Transformer) | No | Simulation only | No | The process model (environment) and testbed are the same |  | Canada; US | University of British Columbia; Columbia University
174 | 174 | Field demonstration and implementation analysis of model predictive control in an office HVAC system | Blum, D; Wang, Z; Weyandt, C; Kim, D; Wetter, M; Hong, TZ; Piette, MA | Blum, David; Wang, Zhe; Weyandt, Chris; Kim, Donghun; Wetter, Michael; Hong, Tianzhen; Piette, Mary Ann | 2026-07-15 | 2022 | https://doi.org/10.1016/j.apenergy.2022.119104 | Model predictive control; HVAC; Modelica; Optimization; MPCPy | CO | Applied Energy | Despite many simulation/field studies showing MPC benefits, practical implementation effort, data quality/availability, and industry risk aversion still block adoption. Few papers quantify the engineering effort or document deployment challenges in real buildings. | 1. Review real-building MPC implementations; 2. demonstrate an open-source Modelica + MPCPy toolchain in a real office with UFAD; 3. document practical challenges and break down implementation effort; 4. quantify performance (energy/comfort) from a 2-month field trial. | Subsystem | Rooftop unit system | Subsystem | White-Box | R2C2 thermal model with solar/internal gain fractions; Modelica HVAC system model | Aggregated zone groups with weighted core/perimeter temps; return fan flow = supply fan flow | No | - | Yes | Real data | MPCPy, Optimica | Modelica | Real building | LBNL Building 59, Berkeley, CA; UFAD with 4 RTUs, UFTs, VFD fans; ~6,038 m² offices | - | - | - | - | - | - | - | - | - | - | - | ALC SOAP API integration, Watchdog & selector logic in BMS, Raspberry Pi + DS18B20 sensors; InfluxDB project DB, ALC WebCTRL, tmux, cron, Docker | 10min | Setpoints for Supply-air temperature, supply fan flow/speed, and outside-air fraction; DX compressor signal; Hot-water valve position | Medium, Low | Daily HVAC energy (panel power + reheat/COP), thermal discomfort (degree-K·h vs setpoints), operational feasibility | Existing BMS control (“MPC OFF”) alternating weekly with MPC | Yes | Full-scale real-world deployment | Yes | Model representation limit |  | USA | Lawrence Berkeley National Laboratory
175 | 175 | An adaptive model predictive control scheme for energy-efficient control of building HVAC systems | Tingting Zeng, Prabir Barooah | Tingting Zeng, Prabir Barooah | JUN | 2021 | https://doi.org/10.1115/1.4051482 | air conditioning, building, control systems, dynamic systems, energy, optimization, simulation, smart buildings, thermal comfort | CO | Journal of Engineering for Sustainable Buildings and Cities | MPC for HVAC can save energy, but practical adoption is hampered by lack of autonomy: models drift over time, identification often needs expert re-tuning, and non-convex MPC planners can fail or be infeasible in operation. The paper targets an MPC scheme that can run long-term without human intervention while handling internal disturbances. | 1. Propose an adaptive MPC architecture that (a) periodically re-identifies a stable, physics-consistent linear thermal model and internal heat-gain disturbance from data using a convex ID method, and (b) uses a convexified MPC planner (via CCP) with descent/convergence guarantees. 2. Evaluate over ~1 year in simulation to show both periodic model/disturbance updates and convex planning are necessary for reliable energy savings and comfort vs a baseline controller. | Subsystem | Indoor air temperature | Component | Gray-Box | Second-order linear state-space model | Humidity ignored; conditioned-air temp fixed at 12.8 °C; OA ratio fixed | Yes | Fan power (quadratic in flow), cooling power (chiller power with COP, uses mixed-air vs coil temp), reheat power | Yes | Simulated data | CVX, IPOPT | MATLAB | Virtual testbed | Nonlinear time-varying RC ODE model (two thermal nodes: zone & wall) with large, aperiodic internal heat load emulating a university auditorium (Pugh Hall, UF) served by an AHU | Building thermal | Component | White-Box | Physics ODE/RC network with time-varying parameters | Time-varying parameters tuned from literature; ignores humidity dynamics; OA ratio fixed | Yes | Fan power (quadratic in flow), cooling power (chiller power with COP, uses mixed-air vs coil temp), reheat power | No | None | N/A | MATLAB | - | 15min | Supply airflow rate, supply air temperature setpoints | Medium | Site EUI (kBtu/ft²·yr), RMSE of temperature violation, max temperature violation; qualitative comfort tracking plots. | Single-maximum baseline controller; Ablations: NAdapt-NCVX, NAdapt-CVX, Adapt-NCVX. | No | Simulation only | Yes | Model representation limit |  | USA | University of Florida
176 | 176 | Virtual testbed for model predictive control development in district cooling systems | Laura Zabala, Jesus Febres, Raymond Sterling, Susana López, Marcus Keane | Laura Zabala, Jesus Febres, Raymond Sterling, Susana López, Marcus Keane | SEP | 2020 | https://doi.org/10.1016/j.rser.2020.109920 | District cooling, MPC, Modelling, Modelica, Machine learning, Testbed | CO | Renewable and Sustainable Energy Reviews | Most DC (district cooling) optimization studies model only compressor chillers, idealize chiller dynamics, use long (hourly/annual) discretization, and lack real-time MPC on hybrid plants with absorption + compressor chillers. This causes time-response issues for slow absorption chillers and ignores detailed dynamic behavior. | Build a virtual testbed / digital twin of a DC production plant (with absorption + compressor chillers) to (i) develop a reliable yet fast predictive model for MPC and (ii) simulate MPC operation vs. a cascade baseline to assess tracking and energy savings. | Subsystem | Chiller plant | Subsystem | Black-Box | MIMO-ARX, convert to state-space (SS) for MPC | For plant-level MPC modeling and simulations: absorption chiller treated as zero electrical power with always-available heat (effectively infinite capacity); pumps ideal; chillers kept in standby (minimum flow) rather than fully off; network return temperature constrained (12–14 °C); ambient temperature varied randomly within 20–40 °C. | No | - | Yes | Simulated data | CasADi, IPOPT | Python | Virtual testbed | Based on Basurto Hospital DC plant (Bilbao, Spain): 4 chillers (1 water-cooled absorption “York” with slow (~3 h) dynamics; 3 compressor chillers—1 water-cooled “Trane” medium (~15 min), 2 air-cooled “McQuay” fast (~5 min)); small TES in parallel; DH with cogeneration provides heat for absorption chiller. | Chiller plant | Subsystem | White-Box | Detailed Modelica components | Standard Modelica modeling | No | - | Yes | Real data | District Cooling Open Source Library | Modelica | - | 5min | Chiller outlet temperature set-points and individual chiller flow-rate set-points | Medium | Supply temperature tracking error (vs. target) and primary/electrical power consumption of chillers | Fixed chiller sequencing (most→least efficient; absorption first), fixed nominal flows, fixed 7 °C supply temperature; chiller count chosen by demanded flow ranges. | No | Simulation only | Yes | Model representation limit |  | Spain; Italy; Ireland | Fundación Tekniker; R2M Solution SRL; National University of Ireland
177 | 177 | Closed-Loop Identification for Model Predictive Control of HVAC Systems: From Input Design to Controller Synthesis | Valenzuela, PE; Ebadat, A; Everitt, N; Parisio, A | Valenzuela, Patricio E.; Ebadat, Afrooz; Everitt, Niklas; Parisio, Alessandra | SEP | 2020 | http://dx.doi.org/10.1109/TCST.2019.2917675 | HVAC; Heating systems; Ventilation; Computational modeling; Buildings; Temperature measurement; Controller synthesis; heating; ventilation; air conditioning (HVAC) systems; input design; model predictive control (MPC); system identification | CO | IEEE Transactions on Control Systems Technology | Existing MPC implementations for buildings often (i) omit the dynamics of HVAC subsystems (heating & ventilation with their local controllers), (ii) rely on empirical PI tuning, and/or (iii) use models that are either too inaccurate (hurting performance) or too complex (hurting tractability). This limits multivariable supervisory control where multiple setpoints (e.g., supply air temperature and airflow) are optimized jointly under uncertainty | 1. Identify data-driven open-loop dynamics of heating & ventilation subsystems and design local controllers; 2. re-identify closed-loop dynamics and embed them in a linear supervisory MPC/SMPC; 3. use graph-theoretic optimal input design to maximize information in experiments; 4. experimentally validate local controllers on a real HVAC test bed and evaluate MPC variants via simulation | Subsystem | Indoor air temperature, IAQ, Heating and ventilation system | Subsystem | Black-Box | Prediction Error Method (OE, BJ), transfer functions/state-space; closed-loop re-identification; H∞/loop-shaping controller design | Linear time-invariant approximation; subsystem temperature dynamics assumed independent of occupancy | No | - | Yes | Real data | System Identification Toolbox, Robust Control Toolbox, CPLEX | MATLAB | Virtual testbed | Same to process model | Indoor air temperature, IAQ, Heating and ventilation system | Subsystem | Black-Box | Prediction Error Method (OE, BJ), transfer functions/state-space; closed-loop re-identification; H∞/loop-shaping controller design | Linear time-invariant approximation; subsystem temperature dynamics assumed independent of occupancy | No | - | Yes | Real data | N/A | MATLAB | - | 10min | Mass airflow rate, supply air temperature, radiator mean temperature | Medium | Thermal energy use / energy savings and comfort | MPC-no CL (no closed-loop subsystem dynamics) vs MPC-CL vs SMPC-CL | No | Simulation only | No | The process model and testbed are the same |  | Sweden; U.K. | KTH Royal Institute of Technology; The University of Manchester
178 | 178 | Modeling of HVAC Systems for Fault Diagnosis | Qiu, AB; Yan, Z; Deng, QW; Liu, JL; Shang, LL; Wu, JS | Qiu, Aibing; Yan, Ze; Deng, Qiangwei; Liu, Jianlan; Shang, Liangliang; Wu, Jingsong |  | 2020 | http://dx.doi.org/10.1109/ACCESS.2020.3015526 | Buildings; Fault diagnosis; Analytical models; Atmospheric modeling; Mathematical model; Energy consumption; Data models; Fault diagnosis; state space model; HVAC system; faults effect analysis | FDD | IEEE Access | Analytical model–based FDD methods are seldom applied in HVAC because of the difficulty of building and validating explicit models at system scale. Existing works focus on subsystems (AHU, VAV) and often lack validation with real/practical data. | 1. Develop a TRNSYS model of a multi-zone HVAC system based on practical building data. 2. Derive and validate a state-space model (analytical, physics-based) against TRNSYS. 3. Model and simulate typical HVAC faults (stuck actuator, pipe scaling, sensor faults). 4. Analyze fault effects on both comfort (zone temperatures) and energy consumption. 5. Discuss future research directions for model-based FDD in HVAC. | Subsystem | VAV system | Subsystem | White-Box | State-space model derived from thermal-mass balance and airflow equations. | Chiller simplified (chilled water temp set directly). Linear thermal-mass balance with bilinear input interactions. Solar gains only applied to south-facing rooms. | No | - | Yes | Simulated data | N/A | MATLAB | Virtual testbed | TRNSYS model of an office building in Shanghai; VAV system with AHU and 4 VAV zones | HVAC system | Whole System | White-Box | TRNSYS building energy simulation | Standard TRNSYS modeling | No | - | Yes | Validated platform | TRNSYS-HVAC Library | TRNSYS | - | 36s | - | - | Zone thermal comfort (temperature deviations). Energy consumption of fans and pumps under faulty vs. fault-free conditions. | Fault-free operation compared with faulty cases. | No | Simulation only | Yes | Model representation limit |  | China | Nantong University
179 | 179 | Practical factors of envelope model setup and their effects on the performance of model predictive control for building heating, ventilating, and air conditioning systems | Blum, DH; Arendt, K; Rivalin, L; Piette, MA; Wetter, M; Veje, CT | Blum, D. H.; Arendt, K.; Rivalin, L.; Piette, M. A.; Wetter, M.; Veje, C. T. | 2026-02-15 | 2019 | http://dx.doi.org/10.1016/j.apenergy.2018.11.093 | Model predictive control; Building simulation; HVAC; System identification | CO | Applied Energy | Prior work rarely isolates how practical model-setup factors (e.g., model structure/order, identification algorithm, parameter bounds, data length/quality, software chain) affect model accuracy and, crucially, MPC performance | 1. Review model-setup factors; 2. quantify each factor’s impact on accuracy via extensive simulations; 3. propagate resulting models into MPC and compare operating costs vs a conventional controller; 4. make models/data/software public for repeatable studies. | Subsystem | Building thermal | Component | Gray-Box | RC network (R1C1, R3C3, R5C4) in continuous-time SS | Well-mixed zone air; linear time-invariant envelope dynamics; gains lumped via effective areas; resistances/capacitances lump building elements; HVAC injects/extracts heat directly to air. | No | - | Yes | Simulated data | MPCPy, Optimica, CasADi, IPOPT, ModestPy | Python | Virtual testbed | ASHRAE/ANSI BESTEST single-zone lightweight (Case 600) and heavyweight (Case 900) envelopes with simple HVAC | Building thermal | Component | White-Box | BESTEST implementations in Modelica Buildings Library | Standard BESTEST constructions; constant infiltration; simple heater/cooler coupled to zone air; office schedules as specified. | No | - | Yes | ASHRAE Standard 140 | Modelica Buildings Library, JModelica for FMU | Modelica | - | 1h | Room temperature setpoint | High | Operating cost under dynamic electricity price with comfort enforced as hard bounds | Conventional dual-setpoint proportional feedback controller. | No | Simulation only | Yes | Model representation limit |  | USA; Denmark; France | Lawrence Berkeley National Laboratory; University of Southern Denmark; Engie Axima
180 | 180-A | Model predictive control of a thermally activated building system to improve energy management of an experimental building: Part I—Modeling and measurements | H. Viot, A. Sempey, L. Mora, J.C. Batsale, J. Malvestio | H. Viot, A. Sempey, L. Mora, J.C. Batsale, J. Malvestio | AUG | 2018 | https://doi.org/10.1016/j.enbuild.2018.04.055 | Low order model; Building parameter identification; Instrumentation; Model predictive control | CO | Energy and Buildings | Existing floor heating control strategies for TABS are often reactive, with fixed schedules or heating curves, and lack the ability to anticipate thermal inertia or free heat gains. There is also a lack of validated, low-order models that are accurate enough for MPC but simple enough for real-time implementation. | 1. Develop and identify a compact, gray-box dynamic model of a real TABS-equipped building zone using targeted excitation and sensitivity analysis. 2. Implement MPC based on this model to optimize FHS supply temperature over a 24 h horizon, anticipating weather/occupancy and balancing comfort with energy efficiency. 3. Compare MPC experimentally and via seasonal simulations against conventional control strategies. | Subsystem | Building thermal | Component | Gray-Box | Lumped-parameter RC (5R4C) state-space model; parameters identified via constrained least-squares (fmincon) and pruned with Morris sensitivity analysis. | Lumped thermal masses for air, slab, walls. Linear heat transfer via resistances for conduction, convection, and radiation. | No | - | Yes | Real data | Optimization Toolbox | MATLAB | Real building | SYNERGI experimental building in France; 200 m² conference room with hydronic floor heating (slab-embedded pipes), 3 fan-coil units, dual-flow AHU, automated metering for thermal/electrical data. | - | - | - | - | - | - | - | - | - | - | - | Sensors: temperature, external conditions (temperature, solar radiation), occupants’ behavior (presence, windows/doors openings); BEMS; Box controller; USB dongle; X2D/X3D protocol; Modbus RTU; Modbus TCP/IP; Ethernet switch/gateway; Remote optimizer (XML, Internet) | 10min | FHS (floor heating system) supply water temperature | Medium | Comfort hours outside setpoint band, energy consumption (FHS + FCU), relative/absolute seasonal savings. | Continuous low-base heating curve (no anticipation); Fixed-restart heating curve before occupancy. | Yes | Full-scale real-world deployment | Yes | Model representation limit | \ | France | University of Bordeaux | \
| 180-B | Model predictive control of a thermally activated building system to improve energy management of an experimental building: Part II - Potential of predictive strategy | H. Viot, A. Sempey, L. Mora, J.C. Batsale, J. Malvestio | H. Viot, A. Sempey, L. Mora, J.C. Batsale, J. Malvestio | AUG | 2018 | https://doi.org/10.1016/j.enbuild.2018.04.062 | TABS, Floor heating system, Energy management, Optimal control
181 | 181 | Optimal design of fractional-order PID controllers for multi-input multi-output (variable air volume) air-conditioning system using particle swarm optimization | Naeimeh Nasirpour, Saeed Balochian | Naeimeh Nasirpour, Saeed Balochian | APR | 2016 | https://doi.org/10.1080/17508975.2016.1170659 | Fractional-order PID controller, multi-input multi-output (MIMO) systems, PSO algorithm, VAV system | CO | Intelligent Buildings International | 1. Traditional PID control in VAV (Variable Air Volume) HVAC systems can be suboptimal due to system coupling, leading to performance degradation. 2. Need for improved tuning methods that are simple, robust, and can handle multivariable interactions effectively. 3. Lack of optimized fractional-order PID (FOPID) implementations for VAV systems using advanced optimization algorithms. | 1. Develop a decoupled FOPID controller for a multi-input multi-output VAV air-conditioning system. 2. Use Particle Swarm Optimization (PSO) to optimally tune the controller parameters. 3. Compare PSO-FOPID against PSO-PID and GA-PID in simulation for performance improvement. | Subsystem | VAV system | Subsystem | White-Box | Physics-based transfer function model derived from component heat and mass balance equations. | Ideal air behavior and perfect mixing. Constant pressure. Negligible thermal storage in some components. Negligible infiltration/exfiltration. Negligible transient effects in flow splitters/mixers. | No | - | No | None | Particle Swarm Optimization Research Toolbox | MATLAB | Virtual testbed | Simulated VAV air-conditioning system based on the same subsystem transfer function model described above; includes heat exchanger, air fan, ductwork, valves, mixing air components, and thermal-space. | VAV system | Subsystem | White-Box | Physics-based transfer function model derived from component heat and mass balance equations. | Ideal air behavior and perfect mixing. Constant pressure. Negligible thermal storage in some components. Negligible infiltration/exfiltration. Negligible transient effects in flow splitters/mixers. | No | - | No | None | N/A | MATLAB | - | N/A | Chilled water valve position, Fan speed | Low | Overshoot (MP), Rise time (Tr), Settling time (Ts), ITSE (Integral of Time-weighted Squared Error) | GA-PID controller, PSO-PID controller | No | Simulation only | No | The process model (environment) and testbed are the same |  | Iran | Islamic Azad University